## Governance Reporting
Water Safety Joint Working Group Action Plan as at 8 February 2017 on Recommendations from the Inquiry Panel
|  | RECOMMENDATIONS | ACTION | RESPONSIBILITY | TIMELINE | RISKS / COMMENT / UPDATE | STATUS: Red (off-track); Amber (on-track with issues); Green (on-track)
Column3 | Column32 | Column12 | Column4 | Column5 | Column6 | Column7 | Column8
a) |  | The joint working group (Water Safety JWG), which has been set up with representatives from HDC, HBRC, DHB and the Drinking-Water Assessors (DWA), continue its work with each of its members committing to co-operate with each other and work positively in the interests of drinking-water safety. | Terms of Reference and 'Ground Rules' for JWG provisionally agreed - to be updated and approved at January meeting. Napier City Council to be invited to participate Status, ongoing utility/value of group to be reviewed within 12 months | Chair | 2017-01-01 | Refer Nathan Gedye letter 5 Dec issue #2 Have invited Napier City Council to attend and they have accepted. Need to get agenda and background to Wayne Jack in advance of next meeting. Ground Rules: Spoke to Nathan Gedeye in regards to transparency around minutes and Action Plan. He was relaxed about a good transparency process. I propose therefore, after discussion on the 19th, to make minutes and Action Plan transparent to the public and media by publishing on one or more websites.
b) |  | The Water Safety JWG meet regularly, and as frequently as required, to maintain effective oversight of all issues relating to the safety of the Havelock North drinking-water supply for at least the 12 months from 12 December 2016. | Monthly meetings to be scheduled - potentially third Thursday of each month - for 12 months Chair to call additional meetings as required | Chair | 2017-01-01 | Agreed 3rd Thursday of each month as follows: Jan 19th, Feb 16th, March 16th, April 20th, May 18th, June 15th, July 20th, Aug 24th (4th Thurs as in China on 3rd), Sep 21st, Oct 19th, Nov 16th
c) |  | The Water Safety JWG members notify each other, and keep each other informed, of any information that could affect drinking-water-safety risks | Members to individually consider WHAT information should be shared - as both a sender and receiver of information Members to provide information to Secretariat by Friday 13 Jan 17 for consolidation. Consolidated responses can then be considered and agreed at Jan meeting. Framework on HOW such information will be shared will then be developed and distributed | Members Secretariat Chair | 2017-01-01 | Keen to include Communications HOD from each council/DHB in this discussion. Have discussed with each CE who agree. Keen to discuss on 19th, but propose a meeting with comms reps to advance together with "Comms Strategy" (below).
d) |  | The Water Safety JWG investigate aquifer matters of potential relevance to drinking-water safety over the next 12 months. | Members to be provided with a presentation on what is currently being done (include modelling) by HBRC HBRC to provide details of presentation (format, venue, date etc) by 13 Jan 17 for consideration at Jan meeting Issues/gaps that still need to be addressed to then be identified by members JWG to discuss/agree how these gaps/issues will be addressed and in what priority order | HBRC | 2017-01-01 | Refer Nathan Gedye letter 5 Dec issue #1 Need to ensure JWG integrates with (but not duplicates) work being undertaken by TANK Potential planning, budgeting and policy issues could come up through this process, which will need to be referred to appropriate agencies eg Drinking Water protection ZonesHBRC groundwater model presented to the group on the 19th. Copies of the presentation provided to all members. HBRC will continue to pursue with the group what application it sees for the model in assessing risks to drinking water supplies, and what scenarios need to be examined. This work will be ongoing for sometime and is intended to feed into the collaborative policy development process (TANK).
e) |  | The Water Safety JWG investigate whether the Havelock North reticulation and distribution systems are fragile or vulnerable and whether they need maintenance, repair work, or improvements, in order to deliver safe drinking water to consumers. | A FRAMEWORK & TIMELINES to be provided that covers current asset assessments, practices and processes in place, risks and mitigation plans, effects of chlorination and hydraulic modelling, for review | HDC | 2017-02-01 | Available documents:HDC Asset Management Plan, independent review on AMP, Hansen Mtce reports, asset reports (age, material, date) spatial distributions, critical assets. Contractor work practices, 3rd party damage risks. Retic performance using current modelling and water quality through monitoring (DBPs, biofilm etc.). | Question as to who will assess and provide independent advice to JWG (Waugh Infrastructure?)
f) |  | Following inspection and any necessary maintenance and/or repair work on the Brookvale bore 3 equipment, the Water Safety JWG should approve the condition of Brookvale bore 3 prior to its use as a drinking-water supply. | Full report to be provided for consideration by 23 Dec, and discussion/approval at Jan meeting | HDC | 2017-01-01 | Current plan to have Bore 3 operational by the middle of February 2017. Reports on BV 3 include bore casing inspection reports (Honnor Well Drillers and RDCL). Reports appended include: Completion of the Brookvale Road No 3 bore report.msg, Brookvale 3 Headworks Inspection and Testing.msg Brookvale # 3 Report 17-01-2017.pdf 160605214_Brookvale Road Bore 3 Investigation.pdf 160605214_Appendix C - Calibration Certificates.pdf 160605214_Appendix A - Geophysical Logs .pdf, 160605214_Appendix B - Field Logging Notes.pdf | T&T report on dye tracer testing and completion of investigation.
g) |  | The Water Safety JWG should, prior to its use as a drinking­ water supply, approve a maintenance and inspection schedule for Brookvale bore 3 for at least the 12 months from 12 December 2016. | Full report to be provided for consideration by 23 Dec, and discussion/approval at Jan meeting | HDC | 2017-01-01 | Refer Nathan Gedye letter 5 Dec issue #4. This will be part of the documentation from suppliers, designers and DWA. Current work completed includes Hazop Study (MWH, HDC, Controlbox), Functional Description Workshop (MWH, HDC, Controlbox and H2ope). FD is approximately 90% complete. Refer Timeline.pdf for current programme at 260117. Timing is best outcome, risks relate to daily tasks remaining on schedule, BV3 testing (including dye testing), commissioning process, and final approvals. Plant will not go fully operational without all approvals. | On track for mid Feb plant commissioning.
h) |  | For at least the 12 months commencing 12 December 2016, log 5 level of treatment be applied to Brookvale bore 3 drinking water (being cartridge filtration, UV and chlorination), with the Water Safety JWG to: | Specific issues i) and ii) to be intially addressed in full report as set out below, with ongoing monitoring/compliance to be included in regular monthly reporting Standard template for monthly monitoring/compliance report to be developed, to include issues raised in recommendations i) and j) below. | HDC | 2017-01-01 | Refer Nathan Gedye letter 5 Dec issue #5 | To apply post activation of treatment plant
| i) | approve the selection and commissioning of the equipment; and | Full report to be provided for consideration by 23 Dec, and discussion/approval at Jan meeting | HDC | 2017-01-01 | HASTDC001-TM1-2.pdf BROOKVALE-P+ID 16JAN2017.pdf UV-Plant-22DEC16-Revision-G.PDF Filters-Rev-E-11JAN17.pdf Filter-UV-Plant-Layout-Revision-D-11JAN17.pdf | On track for mid Feb plant commissioning.
| ii) | oversee the training and operational procedures for the treatment equipment and processes | Full report to be provided for consideration by 23 Dec, and discussion/approval at Jan meeting | HDC | 2017-01-01 | Operations and maintenance manuals from suppliers. FD and updates once plant is operational (mid Feb). Set up meeting with Rotorua DC operators on UV treatment/operations/maintenance. | Initiate meeting in 2nd half Feb.
i) |  | For at least the 12 months commencing 12 December 2016, the Hastings water will be treated with chlorination, and that the Water Safety JWG should keep under review the nature and extent of treatment required to ensure the safety of the Hastings water being supplied to Havelock North | Issue to be considered as part of regular monthly review of a monitoring/compliance report | HDC | Monthly | Refer Nathan Gedye letter 5 Dec issue #8 HDC have agreed. Updates will be provided as new information comes to hand. | Ongoing
j) |  | For at least the 12 months commencing as soon as practicable (but before Brookvale bore 3 is reactivated), monitoring and testing of the Havelock North and Hastings drinking-water supplies take place in accordance with the recommendations of Dr Fricker dated 6 December 2016 and, in particular, that the following minimum monitoring shall be carried out: | Issues to be considered as part of regular monthly review of a monitoring/compliance report HDC to provide draft template for monthly reporting by 13 Jan 17 for discussion at Jan meeting Once commenced, monthly reports will need to be available at least two full days before each meeting | HDC | Monthly | Refer Nathan Gedye letter 5 Dec issue #6 HDC monitoring programme in accordance with specification and DWA approval. V2.1 of the plan previously provided to the inquiry is being updated currently for DWA and JWG approval
| i) | 2-litre raw water samples be taken daily from each bore contributing to the supply of Havelock North drinking water; | HDC and DWA to document concerns/alternatives to testing protocol - Chair to forward to Inquiry for consideration. Monitoring/compliance report to be produced/reviewed monthly | HDC/DWA Chair | 2017-01-01 | Process in place with WTHB. HDC, WTHB, and DWA have concerns re Dr Frickers teating protocol. Recommendation and intention is to take 2 separate samples 1 2litre sample that will be tested using membrane filtration (an approved NZDWS test) on the full 2litre sample and enumerate this. And take a clean 100ml sample (as per typical std) and enunermate this. The concern was the double handling of the 2l sample, and using absence/presence on 1.9l and enumerate the separated 100ml. The intention is to start this during the week beginning the 30 January 2017. Water Testing Hawkes Bay will do this work as ARL have indicated no interest. | The intention is to start this during the week beginning the 30 January 2017
| ii) | total coliform and E.coli testing, using either Colilert 18 or such other effective and speedy test that the DWA approves; | DWA to advise/agree appropriate targets Monitoring/compliance report to be produced/reviewed monthly . | DWA HDC | 2017-01-01 | Process in place with WTHB. | Underway
| iii) | enumerated tests for all reticulation samples and presence/absence testing for the 2 litre samples from the bores; | Monitoring/compliance report to be produced/reviewed monthly . | HDC | Monthly | Process in place with WTHB. | Results shared daily
| iv) | testing from the reticulation sites be continued in accordance with the DWSNZ and the requirements of the DWA; | DWA to advise/agree appropriate targets Monitoring/compliance report to be produced/reviewed monthly . | DWA | 2017-01-01 | Refer Nathan Gedye letter 5 Dec issue #9 A revised sampling plan has been submitted for DWA approval which is still 200% of DWSNZ requirement, the final detail site programming is to be finalised. The current higher level of reticulation sampling will continue until the details of the 200% rate is finalised and agreed with the DWAs | new plan being finalised, continuing at higher level in meantime
| v) | daily testing of FAC levels take place at the ends, and in the dead ends that are most at risk, of the reticulation with a pH level of less than 8 and with a required FAC level of at least 0.2mg/L, or an adjusted level if the pH level is greater than 8; | Monitoring/compliance report to be produced/reviewed monthly . | HDC | Monthly | Included in the revised sampling plan. | Results shared daily
| vi) | testing for disinfectant by-products take place as directed by the DWA; and | DWA to advise/agree appropriate targets Monitoring/compliance report to be produced/reviewed monthly . | DWA | 2017-02-01 | This is about to commence subject to sign off on the locations and frequency for sampling.
| vii) | the test set out in (i) be carried out three times a day during and immediately after an abnormal wet weather event (this event, and the details of such increased testing, to be defined and prescribed by the Water Safety JWG). | Pragmatic definition of what constitutes an abnormal wet weather event agreed - 'When flow in the Mangateretere reaches a trigger point' - trigger point to recommended by HBRC in consultation with Science Caucus | HBRC | 2017-01-01 | Science caucus are to discuss this at its meeting of 25 Jan. No trigger has yet been discussed or agreed to as yet. Assumption made that this only applies to the Brookvale Bores - clarification required from Inquiry in due course - Chair DWA to provide advice on potential 'continuous monitoring of secure bores' options, should Hastings Bores be included Note correspondence below with Nathan Gedeye. 3 x daily only relates to Brookvale. See below email stream:Chris Briefly ( i am on the road) 3x daily only applies to Brookvale- i emailed parties' lawyers to this effect. Nathan Sent from my iPhone Nathan At the meeting of the JWG on Wednesday, a question was raised about the scope of recommendation j) (vii): • The test set out in (i) be carried out three times a day during and immediately after an abnormal wet weather event (this event, and the details of such increased testing, to be defined and prescribed by the JWG) It was noted that j) (i) refers to ‘each bore contributing to the supply of Havelock North drinking water’ (which could potentially include all HDC bores), but it was also noted that the potential impact of an abnormal wet weather event has only been an issue for the Brookvale Road bores. The question therefore is: • Does j) (vii) relate to ALL HDC bores contributing to the Havelock North supply, or just the Brookvale Road bore 3 (once commissioned). We would appreciate your advice on this. Thanks in advance, Chris | Science panel to consider the trigger point, JWG discussed a simple trigger such as 1:10yr rain event
k) |  | For at least the four months commencing 12 December 2016, testing and monitoring for protozoa shall be carried out at each bore weekly using 1,000 litre samples, with the regime thereafter to be subject to review by the Water Safety JWG for frequency but still using 1,000 litre samples. | Monitoring/compliance report to be produced/reviewed monthly . | HDC | Monthly | Programme is about to commence. Have been awaiting manufacture of additional sampling kit to ensure we can meet daily demands. WTHB have been working with Massey to enable this to occur | about to commence larger samples
l) |  | For the purpose of recommendation (k) above, the Eastbourne bores 2 - 5 should be treated as one bore. | Bore number 5 selected for monitoring protocol | HDC | Completed | Advised verbally by HDC at Dec 16 meeting | Agreed
m) |  | The Water Safety JWG satisfy itself that persons carrying out sampling and testing are properly trained and competent, that the testing methods being used are as sensitive and effective as practicable, and that the test processes are being carried out in a way that is optimal in terms of timing, efficiency, and result­ reporting. | Full report covering relevant issues to be produced, to potentially include unit standard qualifications of persons taking samples, IANZ accreditation status of testing laboratories, process map and programme | HDC | 2017-02-01 | Brief paragraph to be provided asap to provide approriate assurance, particularly prior to recommissionong of Brookvale Bore 3. All sampling and testing for compliance is being undertaken by laboratories that are IANZ accredited and to approved processes.
n) |  | An Emergency Response Plan be drafted by HDC and approved by the Water Safety JWG and the DWA before Brookvale bore 3 supplies drinking water to the reticulation. | Plan to be produced, considered and approved | HDC | 2017-02-01 | In progress, will need to incorporate updates to WSP and any specific plans for the treatment plant. Intention is to base this on US EPA guidance document as this template provides a simple way to consolidate the key items. This will sit within Councils wider response planning framework- but be Water specific | In production
o) |  | If the Water Safety JWG is unable to reach unanimous agreement in relation to any matter pertaining to the safety of drinking water, advice to the Inq uiry of that should be given promptly by the Water Safety JWG Chair to counsel assisting the Inquiry. | Acknowledged | Chair | Ongoing | Nothing to report
p) |  | Brookvale bores 1and 2 should not be reactivated for drinking-water supply without at least six weeks prior notice to the Inquiry and the Water Safety JWG | Noted | HDC | Ongoing | Both bore pumps have been removed for inspection and checking of bore casings. Plan is to clean and refurbish pumps but not to reinstall unless approval is sought. HBRC was advised that BV1 is proposed to be abandoned and not used again. BV2 however may be used. Both BV2 & 3 would need to be reconsented before May 2018. Therefore it will be important that HDC begin discussions ASAP with HBRC to ensure a robust reconsenting process.
|  | OTHER ISSUES | ACTION | RESPONSIBILITY | TIMELINE | RISKS / COMMENT / UPDATE | STATUS: Red (off-track); Amber (on-track with issues); Green (on-track)
|  | Communications Strategy Whilst communications are generally a corporate issue for each agency represented, agreed that JWG will have a role to play in restoring community trust and confidence | Agreed in general that all agencies releasing communications relating to drinking water will share these with other agencies prior to release, to ensure accuracy and consistency - members to identify the nature and level of such communications Chair to brief agency CEOs on this issue | Members Chair | 2017-02-01 | As above. Have approached all CE's who are happy for all Comms HOD's to be approached for participation in a Communications Strategy in conjunction with involvement on Rec c "What information needs to be shared"
|  | DWA capacity/availability | Confirmation required that HBDHB PHU will provide continuity and sustainability of DWA resource to fulfill local on-site operational requirements, leaving Peter to fulfull secondary/strategic role. | HBDHB | 2017-01-01 | DHB will be increasing contracted DWA resource from 1 week to 2 weeks per month from now until June. This is estimated to be an appropriate level of resource to complete the current workload issues. To be reviewed in May.
|  | 12 Month Review | Agreed that JWG will review the potential ongoing utility and scope of such a group beyond the 12 month timeframe - to be placed on the agenda in late 2017 | Chair | 2017-10-01 | Noted for Agenda - Sept 17
|  | Bore Security | Letter from HBRC to HDC indicating 'possibility that bores covered by resource consent WP070080Tb may not meet condition 21 of that consent in a similar way to to Brookvale bores 1,2 and 3'. HDC seeking to develop a practical approach which enables HDC to undertake appropriate tests that will be recognised and accepted by DWA and HBRC without duplicating effort and cost. | HBRC & HDC | 2017-02-01 | An item for future consideration in March. Working group (DWA, HBRC, HDC, NCC) to develop criteria and process for testing, inspecting, verification and reporting.
|  | White paper on 'Additional Measurement Options' | The HBRC Groundwater Model to be used as the basis of current measures, with a White Paper on 'Additional Measurement Options' to be developed for discussion | HDC | 2017-03-01
NEXT MEETING
Thursday 16 February 2017
9.00am - 11.00am
Venue - Hastings District Council
- 2nd Floor Meeting Room 1