DAY 2 INQUIRY RESUMES ON WEDNESDAY 28 JUNE 2017 AT 9.00 AM

JUSTICE STEVENS:

Just before we start, it has come to the attention of the Head of Secretariat that some members of the public cannot hear, so might I ask counsel to fold there microphones down so they speak into them, that is right, and for the witnesses to keep your voice up so that members of the public can hear, thank you.

mr GEDYE RE-CALLS

CRAIG THEW (ON FORMER OATH)

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Mr Thew, just before we move to another topic, I wanted to ask you briefly about your chlorine-free taps, or the de-chlorinated taps, how many do you have?

- We have three: one by the Hastings Library, one in Havelock North and one in the suburb of Flaxmere.

- Do you accept that there is a significant risk or a significant level of risk in operating these filtered taps?

- Providing this service adds an extra complication and some risks that we have to manage.

- Are these carbon filters?

- My understanding, they are granulated carbon filters and after some initial issues we added a following filter to cleanse out any particular carbon particles.

- Do carbon filters inherently need quite comprehensive hygiene and maintenance programmes to remain safe?

- You need a preventative maintenance programme on them such as a length of time and amount of water that flows through them, a flushing programme which after the initial results we received when we closed them we changed to a flushing every night, but it does require monitoring to keep an eye on potential bacterial growth within the carbon itself.

- And at some past point did you receive or did you have very high HPC counts from these taps?

- That is correct.  Particularly the one in Flaxmere, if I recall.  The first results we received from the brand new tap come back with a remarkably high number and at that point we immediately shut them down, took some advice and some further research and looked to alter the programme of how they were operating.

- Have you looked at installing a UV bulb on each such tap?

- No, we have not looked at that.

- That would give a safer and better result, wouldn't it?

- I would have to take some advice on that and we are – when we can release Mr Deere from this process, that is one of the topics we are talking to him about.  There are different ways of removing chlorine from the system and if we were running a permanently chlorinated system and there was a community desire to have chlorine free taps, there is other processes such as reverse osmosis and like which would have a – would not have some of the issues that the activated carbon, carbon-stripping potentially creates.  I must say, when we went through it we did quite a lot of research and taking that advice and the levels we were getting in referring there is not a significant amount of guidance internationally, but the World Health Organisation Guides did talk around if the water entering that system was safe for drinking, you will expect to get an increase in the HPC level, but if it was safe to drink beforehand, it should be safe to drink afterwards.

- Just as a matter of interest, how popular are these taps?

- Very popular.  I don’t have the exact flow rates with me, but the one particularly in Hastings Central which used to be a fluoride-free tap, used to be tap – used to be connected straight to the artesian pressure of the bore and that was an agreement with the community when we had a referendum which decided to keep fluoride, we converted that location, connected it off the main reticulation, added in the carbon filter to provide the community an option of chlorine-free – it was a very strong push and a desire from the community.  So the ones in Flaxmere and Havelock North are a little less used and that is why we have a nightly flush at 2.00 am every night, but that is something we need to keep an eye on and make sure that that programme is keeping things under control.

JUSTICE STEVENS:

- Does the flush require someone to go out?

- No, it's an automated process Sir.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- All right.  I want to ask you about the Water Safety Plan.  Just been approved, hasn’t it?

- That is correct.

- The matter I particularly wanted to ask about is process control chart.  Has Dr Deere given you advice on the benefit of a process control chart?

- Oh, absolutely.  The team have had long discussions with Dr Deere and actually the process control chart is in creation at this point in time.

- Weill that be added as an appendix or will it change the body of the report – the plan?

- I don’t believe it changes the body of the plan, but it becomes a very useful appendix.  And I think it's a number of improvements, just to change the focus of the Water Safety Plan to really start focus on the control points rather than just highlighting hazards.  Probably a shortcoming in the guidelines is actually a lack of focus on control points and the management of those and highlighting those.

- So do you accept and agree that a water safety plan will be much more use if it is something more than just a risk register?

- I believe the water safety plan is already more than a risk register but the process of doing risk assessment is the critical element there, doing a thorough and detailed risk assessment from multiple perspectives.  The key then is how do you communicate to the different audiences so each audience can understand their role and the control points.

- Isn't the prime audience the operators and the water managers?

- I think there are a number of audiences.  The water operators absolutely are one.  What is their role?  What are the critical control points that they're there to manage?  The water manager, what are the critical control points that they should be watching and managing?  What are the improvements that they need to be developing and getting governance by on at an executive and governance level?  What are the critical control points that governance can be assured are in place, are operational and providing appropriate control between the raw water and the community drinking it?

- So none of those control points are in the current approved document are they?

- I think they are in there but they're not – the format, the tabulated format, if you get to the risk table, is very involved and very detailed and they don’t naturally bring out and I guess that moves on, our thought process of (a), doing risk management in a slightly different way using the bowtie analysis approach, which looks at what's the tipping point event?  What is the tipping point event?  What is the thing that tips that you're trying to not happen?  To that you have a number of hazards which might contribute to the tipping point, so it might be a change in the groundwater condition or if you were a river, there might be something that contaminates the water source.  It might be –

JUSTICE STEVENS:

- Or an earthquake.

- Or an earthquake.

- I mean that sounds to me like a typical tipping point or one that would put a water operator on high alert.

- Yes.  So you have those hazards.  You have that tipping point event so the supply has become contaminated and then what you want to understand is how many control points do I have between that hazard and the tipping point and they're your preventative measures and the higher the risk of that hazard, the more control points you should be looking to have between that hazard and the tipping point and when you then do an analysis of those control points, do you have enough independence between control points.  So a different way of looking at water safety rather than just at the hazards is how many control points should I have between the customer throughout that whole process and actually focus on how many control points and what safety do I have.  On the other side is if the tipping point happens and you lose it, we have consequences and a typical way of doing risk tables, we don’t explore all the potential consequences enough.  We focus on the event.  So what are the potential consequences?  How do we pull those through and then what the control points to mitigate the consequences?  So at the moment, a normal monitoring event is a verification of process but it's also a consequence-managing device of variable use because if the period is too long, obviously the exposure of the community is too long and you might have other mitigating process and obviously contingency plan is a mitigation.  Ideally when you look at that bowtie, you should be having at least two thirds of your focus, if not more, on those preventative measures rather than on those consequence-reducing measures.  So that’s the process we're looking to bring forward and that way at a diagrammatic view you can sort of traffic light it or do something else to the control points into the diagram.  It doesn’t make risk analysis any simpler.  In fact it probably gets you slightly more involved to understand the complex processes but I think that’s absolutely what's necessary 'cos often the devil is in the detail.  It's the small things that can happen that slip through that can create significant public issues.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- So will the bowtie appear as a diagrammatic representation in the water safety plan in lieu – in place of all the existing pages and pages of risk tables?

- As the current legislation stands, there would be a bowtie as well as those tables.  This is an issue we're aware of.  I ran this idea through Dr Deere and I'm sure the Panel or that counsel may ask Dr Deere.  Sydney Water have done an extensive programme following the cryptosporidium outbreak many many years ago.  It was a long-term – it was an extensive project and they're a significant entity.  They are still required, my understanding is in the New South Wales legislation, they still have to have the standard tables because the legislation is a format in which it wants to respond to.  They're little idiosyncrasies I would hope in the New Zealand context we can work through in a more pragmatic fashion.

- Now, under the bowtie approach, would that have picked up the risk of livestock, heavy rain inundation, a pond and transmission into the aquifer?

- The bowtie process or how would it show that?

- Yeah.

- So the framework itself won't highlight anything.  The key is how you facilitate the cross-section of people you involved in those discussions and it's actually really important to bring a diversity of people into those discussions so if you just have the existing team who are used to working in an existing environment, they only see what they see and they understand and they clarify and they filter down to what they know.  So bringing in a diversity of views, diversity of perspective, so when we go through this process, our intent is we would want HBRC involvement in there, health involvement, some community groups, particularly when you work through consequence mapping.  I mean obviously we've learnt a lot the hard way working through and pulling it out but it's diversity of view and it's the thoroughness of the risk assessment.  Quite often people will say oh, that would never happen, when people talk around what else could happen.  My response to them these days is anything and we need to keep our mind open to anything.  So the bowtie process, going back to the question, the bowtie process itself isn't a guarantee to bring out everything.  It's how that facilitated and the people involved that’s important to bring out all of those but for our case, absolutely those catchment elements are a key.

- I can't help asking whether all of that sophistication and complexity could lead to the very simple and the very obvious things being overlooked.  What would you say about that?

- So that’s why you bring in people who aren't – there's always a risk when you have people who are involved with a process in detail to miss the obvious.  That’s an intrinsic problem.  So that’s why you bring in diversity of views and backgrounds, so not everyone technical.  You have a mixture of people in those discussions who can ask the question which might seem silly but people can overlook.  The diversity of view also reduces the issue of group-think where everyone sort of starts heading off in a direction and no one becomes counter-factual in those discussions.  So it's actually how you design and the diversity of those involved that provides a level of protection to that.

JUSTICE STEVENS:

- Could I just add to that?  That might be a really good reason for having access to someone like Dr Deere?

- It's an absolutely exact reason.

- Or his equivalent and particularly with international experience.

- Absolutely.

- Yes.  As opposed to a third party source that has been involved from day one that might be captured by a group-think.

- Yes.

- Or a set way of doing things.

- So the discussions we're having in terms of running this process is a company that we've been working with on the health and safety front helping us do that.  So he's not involved at all in the water industry but very much comes in from that health and safety perspective which is where we're sort of borrowing this concept from.

- Thank you.  And I just have one other point.  Counsel assisting has raised the concept of simplicity and I wanted to check, there is nothing in the Guidelines that would prevent an executive summary in a Water Safety Plan is there?

- I wouldn't believe so and if – it would be a ridiculous thing that would prevent an executive summary.

- And the current one doesn’t have an executive summary?

- That is correct.

- I wonder whether it might be useful and simple if in the next iteration of your Water Safety Plan had an executive summary accompanied by a process control chart?  There's nothing to stop –

- Absolutely, that’s –

- – either of those things and the – rather than burying those simple one pages or two pages in an appendix where people may not find them in a crisis, put them as the front document?

- That’s exactly the advice we are working through with Dr Deere is to bring that right to the front.

- Wonderful, well.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Do you have a copy of the Water Safety Plan in the box there, Mr Thew?

- Not with me, I have got one over –

- There should be on in the –

- Oh, sorry, yes.

WITNESS REFERRED TO water safety plan

- I just wanted to ask you about paragraph 2.6, the event history on page 9, pages 9 and 10.

- Paragraph number?

- 2.6, page 9 of the document and it is headed “event history.”  I hope this plan hasn’t become so long, you can’t find anything in it, Mr Thew?

- Sorry, just –

- Page 9 of the plan, Water Safety Plan.

- The second page 9.  There’s a page – pagination issue in the release document.

- Oh, I see that, page 18 comes before page 10, a zero.  We’ll ask Mr Wood about that later.

- I think he’s already provided some excellent commentary on that.

- Look, all I wanted to ask you is this event history table does not contain the 10 E.coli results you got at Waimarama and other stations and nor does it contain the Frimley 1 and Eastbourne presence readings.  Admittedly, they were in the investigative monitoring system, but it may be you who said a result is a result, however you get it.  Should that table not contain all of those findings?

- So in relation to the Esk and Waimarama, they have their own Water Safety Plans, so that’s a – they’re separate plans to this, so they will have those into those separate plans.  The process is, is there is a separate plan for each scheme.  We have worked through with the DWAs for a number of our schemes around the coastal townships which are very, very similar characteristics, we have combined them and then the risk tables just have if there is something specific, so they’re in complete separate plans.  I take your point just on those investigations that we are working on and any findings that come from those will make their way into the plan if they haven't.

- Well, ideally they should be there, shouldn't they, to provide a complete picture of events, E.coli reading?

- Yes, I think there is some validity in having a – there is, I guess, two levels of events.  One where there has been confirmed issue, but also learnings and investigations sort of summary – summarising learnings, investigations.  Obviously all that makes the document a little bit longer, but I am sure there is a way of summarising those simply.

JUSTICE STEVENS:

- The other point is that if – even if it is the positives of it or transgressions are technically in a different bore which has its own Water Safety Plan, if it is drawing from the same aquifer then surely – and if you, for example, don’t know the cause, wouldn't it be useful?

- Yes, I think it's making sure you’ve got the right thing in the right place.  This table is only part of the process in place of maintaining the history and the knowledge.  A key part of knowledge retention and people understanding is that we're looking at using a story-telling and so part of that is actually creating short little party operations manual as people tend to retain things as stories and listening to operators talk.  So putting into documentation little video clips that actually as new staff come on, they pick up the stories.  That’s far better retained than people having to refer and read a document and recognise the importance, whereas story-telling actually helps bring within people a far better recognition.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Do you support the suggestion made yesterday to Mr McLeod that the water safety plan should be reviewed more frequently than the legislative period?

- My view is it should stay a living document with an annual review and that’s not necessarily implying a full rewrite unless there's some fundamental changes but there should be a process of reviewing the status every year: is this still valid?  Is there anything new that needs to be added?

JUSTICE STEVENS:

- At least annually –

- Yes.

- – is wording that would work?

- Yes.

- In any varied recommendation?

- Yes.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Can I ask you some questions about the Emeergency Response Plan?  Is that an appendix to the water safety plan?

- Yes, it forms an appendix.

- Do you have a copy of it there?

WITNESS REFERRED TO Emeergency Response Plan

- Yes.

- What's the status of the ERP now?  Has it been finalised and approved?

- It will never be 100% finalised.  It's a living document that will take on learnings of events.  The key piece that has been fairly well locked-down is the major contamination contingency plan but even saying that, in our discussions the other day, and I think I've sort of passed this on previously, when we were working with the drinking water assessors, so the DHB have taken that plan, also having the experience of working through that plan at Waimarama and are looking at how that works for their organisation and have come up with some, are working through some good thoughts to help develop that.  So we'll be working with them and the idea is also with Napier City and the Regional Council where it makes sense because there is still an ability where this could be a regional document with general agreements on how to approach it.  Where the plan is lacking is it is the level of graduation between nothing and everything.  So the plan is set up for everything and it's bringing on a little bit more graduation where it doesn’t need to jump to the worst case scenario, whereas the agreed protocol is that okay just take a breath, have a look at this before we jump further and that’s the work that we're working through with Dr Deere and we also need to with the drinking water assessors.

- Does the drinking water assessor actually approve the ERP or not?

- Well, the ERP forms the contingency plans and the contingency plans are referenced in the water safety plan, so in my mind, by proxy, yes.

- Does this ERP now replace your contamination protocol?

- Elements of that contamination protocol will fit into those graduated responses.

- Can't just put my finger on it but I saw a comment somewhere in the ERP that this does not cover instructions for operational steps or something to that effect.  Where does one find those or how do they come into action?

- So that’s where, I think it was in my, the brief of evidence or the just notes.

- Yes.

- Yeah.  So if this document was to turn into a standard operating procedure document, it could get extremely long very very quickly.  So there standard operating procedures.  As part of that work that Mr McLeod talked about, we are going back to review those.  Many of those are working very well and I think that played out in August of how the team mobilised and so quickly got chlorination into the system once that decision was made.  So they're standard operating procedures that need to be owned and understood by the operators.  If they have to read about what to do in an event, it's too late.  The critical control point, the process control points simplified diagrams that Dr Deere’s talking about in the water safety plan, I think that provides a key level of guidance that would fit inside here.

- You have planned a training programme for the ERP, training and refreshing?

- The intent – there is – I currently, as I speak now, there is no programme, training programme, in front, but that is absolute what will happen.  Since the August event, obviously we’ve had some smaller events that we’ve manage – worked through, so those live events have filled the gap of training exercise, but it's important to design a training exercise that picks up on different aspects and different intentions, different parts of the plan.

- Your boil water notice and other parts of your ERP continue to have this inconsistency about how to boil water and it may be a micro-point in this context, but it continues to intrigue that all – the boil water notice and the instructions in the ERP, if you have an electric jug boil until it reaches a rolling and switch off, but if you use a pan you must boil it for one minute.  Are you aware of any reason why an electric jug can just come to the boil, whereas a pan needs to be boiled for a minute?

- The electric jug gets hotter.  So this is the guidance from Ministry of Health and the Word Health Organisation Guidance.   It is also important, you might need to issue a boil water notice when there is no electricity and so all that people are left with is their gas barbecue to boil water or their little primus stove, so the electric jug might not actually be available to the community when a boil water notice is being issued, if there is a widespread power outage.

- But doesn’t boil – doesn’t water boil at the same temperature at sea level?

- Well, a rolling boil starts a little earlier than the 100 degrees.

- It would be desirable not to have instructions that are complicated or confusing to the public, don’t you think?

- The more clarity that can be provided, the better.  This is the guidance that we’ve used and has been supplied, so if there is a different way to say that nationally we would be happy to adopt that.

- I see in the fact sheet in your ERP, the intriguing advice under the heading, “Can I take a bath or shower?”  This is after about page 44 of the ERP, it says that if you have had surgical wounds or chronic illness, you may want to use boiled or bottled water for bathing.  Again, it's a very small point, but that’s not realistic advice is it?  How do you use boiled water or bottled water for bathing?

- I think it's a very difficult circumstance, yes.

- You’d need a lot of bottles, wouldn't you?

- Yes.

- The concept of a precautionary boil water notice devolves the decision whether to boil to the public. Would you agree that it is better to either have a mandatory boil water notice or none at all, so that the public aren’t put in a position of having to make an assessment of whether they boil?

- Sorry, just a precautionary – just where is that?

- Do you have a precautionary boil water notice in your ERP?

- No.  So one of the discussions we have been having with Dr Deere coming from a different jurisdiction is – and across the world there is different ways of doing boil water and they quite often will have an advisory before they go to a notice and in other jurisdictions the boil water notice actually has a legal standing like an unsanitary building notice and if you have more than a certain amount of people in the building the notice must be on a wall.  So one of the ones that we haven’t put into the ERP that was one of Dr Deere’s suggestions is a precautionary boil – a precautionary boil water advisory, I think it is, Mr Deere would be able to comment better – and then moving to a – so they have like a two, two-tier approach.  That doesn’t exist within the New Zealand framework.

JUSTICE STEVENS:

- But is there anything to stop us doing that?

- No, there’s not and I think –

- Let's, you know, do it.  Just if it is sensible.

- Yes, so –

- As long as you meet your requirements under the Guidelines.

- So I think counsel assisting was referring to mandatory so a boil water notice has no legal standing at all and I guess a comment I made through stage 1 is that the guidance on around boil water notice itself between the, what it says and the only reference in the Health Act is around a responsibility or a power of a designated officer and then the Guidelines have some commentary around water suppliers so I think that’s an area that would be usefully developed and the Australian Drinking Water Guidelines, at the request of the water suppliers, actually created a set chapter on issuing a boil water notice and the like which is actually very useful.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Well, if one doesn’t use mandatory in any legal or technical sense and just refers to a notice where it says “you must”, that is the key to a boil water notice isn't it, to be unequivocal and mandatory in a sense of saying, “You must do it.”?  Of course people are free not to.

- The language that applies.

- But you wouldn't find many people who would ignore it presumably?

- Yes.  I mean the language would go a long way too.

- Well, you needn’t be impeded by legal niceties in saying, “You must boil your water.”?

- Yeah.

- You'd agree with that wouldn't you?

- Agreed.

- It is effectively a recommendation but isn't the received body of thinking that you just mandate it and tell people to do it for their own good?

- You issue the notice in a way that most of the population will take it as an instruction on which they have no choice.

JUSTICE STEVENS:

- Well, you could amend the first sentence.  Instead of saying, “The District Council are advising residents and businesses in the affected area to boil,” you would say, “Advising residents and businesses that they must boil.”  Very simple.

- Yes.

- And there are some spelling mistakes on that page as well by the way, so you might want to have another look at page 42.  Middle of the boil water paragraph there is a “the”.  I think it means “then” but this is a work in progress?

- Yes.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Have you had significant input from Dr Deere on this ERP?

- He's had a first go-through and you'll see elements in there where the starter of a decision flow path.  There's a lot of work to carry on doing in terms of creating decision trees for that graduation on the smaller, so the yellow areas of text which are highlighting improvement items, many of them are from Dr Deere that we will be continuing to work through but also strongly aligned to our local drinking water assessors.

- Does the JWG had input into the ERP?

- So the joint working group signed off on the initial version back in February.  They have not, just in delivering this version through to the Inquiry, they have not had input into this particular version, which just has some minor alterations made to it.

- The DHB would be a big part of any emergency.  Have they had input into this plan?

- As I mentioned earlier, we've been in discussions with them.  They have taken away the .04 version that was signed-off in February and have been working it through their own processes and are internally working up a couple of adaptions and we're looking at how we incorporate their thoughts into this and move forward together with it.

- So it sounds like there's still some work in progress on the ERP?

- Yes.  As I said earlier, I believe this, an ERP needs to be just like the water safety plan, a living document and every event creates a learning and you need to sit back and there may not even be a water contamination event or a supply event.  It might be another event that collective agencies are working through where they are learning.  So none of these are things that you’ve finished and can be put on the shelf and forgotten about.

- Is the purpose of this document more to create organisational capability and readiness rather than to be used in an emergency?

- It's a bit of both.

- It's a very –

- Absolutely working through thinking about before the event so you're ready to react during.  But it's important in thinking about potential events, it's thinking about the key principles, what are the aspects that need to be considered rather than fully designing the response because every event has its own idiosyncrasies and every event must be managed on its merits otherwise you will mismanage the response.

- If an emergency happened tomorrow, who would make the decision to issue a boil water notice?  Who has that responsibility?

- So within the plan, myself, the Chief Executive and Mr Chapman.

- Any one of the three?

- Correct, depending on who’s around.  So if I reflect through the Esk which was the last discussion, the last event we had where we had a – that return transgression, the results got called in from the lab, Mr Kersel immediately contacted the DWAs, Mr Chapman and myself.  We issued the boil water notice for the full scheme.  On that evening, Dr Jones, Mr Chapman, myself, we went through “this is the work we need to go, here is the area investigations.”  So the plan worked through, tasked off people to talk to the various elements of the community.

- I want to ask you briefly about the relationship with the DWAs now.  Stage 1 of the Inquiry heard a lot of evidence about a somewhat inadequate response to many DWA letters in years past and DWA requirements and we saw that things weren't auctioned and so-on.  What is the situation today with the DWAs and HDC, how is it working?

- So I think I can give my view, but I think it is important that you also get the DWA’s version of the view.  In my mind, it's in its best operating state and it's probably one of the tightest and most collaborative and forward-thinking of the relationships.  It's moved into a really useful space.  We often end up sort of working through our issues and wider and then start trying to save – add wider views and moving forward so it's very proactive.  There is an agreement and make sure if there are some issues that aren’t getting worked on that they are escalated so they are not just left between a – it's not a lower member of each organisation having a discussion, not going where if that’s the case everyone understands that it needs to be escalated so people can sort it out.  We haven't come across that issue and the monthly operational meetings have been very useful and I know the DWAs are looking at modelling that in their work with the other Water Authorities.  And from that, saw the development of those transgression templates to templatise how to report on events, just to try and make that more efficient and make sure all the key answers are worked through.  The work we are doing with Carly Price, also we’re looking at rather than doing the annual reports or quality reports, some of that compliance report is to look at having that tabled at each monthly meeting, so we’re actually monitoring and managing what is going on throughout the year, so at the end of the year report which all gets collated up for the Ministry of Health and ESR to create the national report, rather than that being all reported at the end of the year it is actually built up as a continuous basis.  So there is a lot of proactive discussions and opportunities being worked through.

JUSTICE STEVENS:

- What do you put the improvement down to?

- A commitment for the same goal and a very strong alignment.  Both all the parties or the core participants here have worked through an event which helps see the new operating environment with far more clarity than I think many of the – much of the country has yet fully realised.  So the tensions of the event and the learnings of the event are shared and we see an opportunity of how it can be made better.

- But would you agree that that, in a sense, is a product or by-product of the Inquiry perhaps operating outside the Inquiry?

- I believe the improvement in the nature of the discussions would have happened in spite of the Inquiry, but absolutely because of the event and – yeah.

- Thank you and you are right, we will want the DWA perspective as well.

- Absolutely.

- Because it is –

- I hope they agree.

- – it is a two-sided matter, isn't it?

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Do you have some visibility as senior management into DWA requests and requirements and what's happening about them?

- At this point in time, I try and attend every one of those operational meetings I can.  I have missed one or two but I attend those meetings where I can and get an update.  I get the minutes from those, of tasks whether I'm at that meeting but I have made most of those monthly meetings myself.

- I want to ask you about the joint working group.  You sit on it and attend the meetings don’t you?

- Yes.

- I think you were here when I asked Mr McLeod about the JWG and I have similar questions for you.  From your perspective, having attended it, how well is it working and what are its benefits?

- I think it's working well.  I think it's going through a genesis.  Very early in the process, it was very, I would describe, transactional as we worked through the Inquiry’s task list and very much at the front end of the work programme there was a heavy load around a number of the compliance check-offs and so forth.  So I think those early days of it were very transactional as we worked through just some set items.  Now as we move into, as been explained, those sort of the White Paper picking up those two key issues, that’s actually where we get into really the meaty and valuable elements in terms of moving forward.  It's also been a very useful exercise just to increase the understanding, a forum, understanding of each other, understanding of what the operating environment each agency has to work in and a chance just to increase those, strengthen the relationships to be able to have those discussions.

- You mentioned the White Paper.  Can you help us with a bit more detail how that is working or how it's supposed to work?  I take it that some of the major tasks that the JWG was asked to perform have now been sent off for the White Paper to be done on them.  Is that right?

- So the approach – so in early meetings of the joint working group, we discussed, sort of in a very high level around what potential items might be and aquifer matters and information that we can share.  There were a number of sort of items thrown around the room in the meeting but it wasn’t sort of just we hadn't designed a process just to collect all those thoughts so the concept of let's start building a White Paper just catching the raw facts was tabled.  Initially I think the task was mine to sort of capture a number of thoughts that I'd tabled but at that point in time, I was more I had other more pressing priorities and that’s where the Regional Council have been really great by providing the resource which can help collate up those thoughts.  So the process we're going through at the moment is, as has already been described, is the HBRC staff member will be, she's working her way round interview processes with a number of questions that the joint working group signed off on the other day of sort of key topics, an area to gain those facts.  Unfortunately that got slightly delayed due to a bereavement in her family so from my part, Mr Chapman and myself have a meeting with her next week or the week after next, I think Monday the week after next actually, to go through those items.  Once that’s collated, then that'll be put through and create a consistent picture and then the group will then work out okay, here's the key elements that need fleshing out more and here's things that can be noted but just parked because it may not be the biggest return.

- Does the White Paper considering the question of aquifer risks or aquifer investigation?

- It considers –

- Is it only that question or what?

- It's primarily focused on the aquifer but I mean one of the key lenses and become clear is around each of the agency holds a lot of data and are each agency aware of all of the data the other one has?  So we have gone through a session where the Hawkes Bay Regional Council ran through the data they held.  This is how you can access the public side.  Here's the stuff that’s not public and then it's reflecting back well, which of that makes sense or is useful from a drinking water perspective because this thing could grow bigger than Ben-Hur.  So one of the elements is what is all the information that everyone has got?  Does that information inform the key questions that we have that will maintain and provide safe drinking water to our wider communities?  So really getting an information of what all – a view of what all the information, what are the responsibilities for each agency for that?  It might be that one agency holds the raw data, but another agency is doing some analysis with it because they’re more interested in the outcome of that.  There might be that the agency who holds the data is doing the analysis and sharing it.  So that’s one element of the white paper and the other one then is, is okay, if there are some things and we’ve been having discussions around potentially looking at the state of environment monitoring and is there some enhancements that can be made.  That would inform actually there might be a gap in knowledge, we’d like to know a little bit more around what is going on here.  But what are risks of the safe drinking water to the community has to be the centre of that next part.

- Can I just test what you are saying by a couple of thoughts.  One is that when you look at the recommendation, it was to investigate aquifer matters of potential relevance to drinking water safety, would you agree that to be relevant to drinking water safety, it's got to be basically in a source protection zone or a catchment that can affect the bores?

- So not – and I guess this is one where there’s another topic we’re working through, and that Dr Jones is quite rightly raised and Dr Jones and I talked around a large proportion of the Hawke's Bay community is not on a municipal supply.  So that is industrial business, food-making premises that are under the guise of MPI and numerous private properties.  So not only is it around aquifer matters that relate to municipal supplies, but thinking more wider for our communities that we have an oversight of, what potential risks exist to individual properties who are sourcing their water directly from the aquifer which really, in many sense, forms a bulk water supply in our Hawke's Bay area.  So –

- But don’t your Health Act responsibilities address network water?

- There are, there are multiple layers in there.  Because under the Building Act a property must have a potable supply.

- Well, in any event, the short answer is you are looking at anyone who consumes water out of the ground in the region, whereas I, I think, was asking about the Havelock North network supply under the Health Act.  So there’s two, one’s a much narrower frame of reference, isn't it?

- I think if we were just looking at Havelock North, most of that work is done and it wouldn't add a huge amount of value to the region by not thinking wider.

- Another question I had, is if you wanted to investigate aquifer matters, would that not really be the province of a hydrogeologist who would do a report on the aquifer?  It's structure, it's movement, it's – there have been such reports, haven't there?

- Absolutely and the Hawke's Bay Regional Council have investigated significantly and have worked through a lot of work around their modelling work which informs the TANK process that has been referenced.  That is the key process which sets out around policy-setting and ideally getting that source protection zone concept and how that work, that would be far better implemented within a policy setting rather than a consent-by-consent basis.  Obviously to set that within a policy setting and a framework, you need to work through making sure you’ve got your rigorous science.  So none of this is in isolation and joining into all that work that GNS and the HBRC science team, ESR who have inputted into it, the work that we are doing with Tonkin & Taylor who are leveraging off many of that work HBRC’s base has created.

- And do you have any concerns that referencing things as broad as SOE monitoring and the whole TANK process is insufficiently relevant to drinking water bores?  Insufficiently connected to it or directly relevant to it?

- No, I think that it's important to do – to look wide because the TANK process is actually a potential key path that creates ongoing, ongoing protection to drinking water, the sources, setting the rules around how bores or risk paths are potentially managed.  That is then transparent to anyone who is looking to apply to develop to invest.  So it think doing that work at a holistic level is absolutely relevant to ongoing and sustained safe drinking water in the Hawke's Bay.

- How long has the tank project been running?

- I wasn’t involved in the start.  I've recently joined into that session, joined one of my colleagues.

- Do you know how long it is proposed to run in future?

- It has a finite process, so you'd be better to confirm that with Mr Maxwell and Mr Palmer.

- And it's Rena Douglas that’s doing this White Paper at the RC?

- That is correct.

- And what do you expect the White Paper to contain when it's finished?

- I would expect it to highlight key considerations that could affect the safety of drinking water.

JUSTICE STEVENS:

- Well, presumably it is going to identify the places within the two organisations where information is held?

- Four organisations.

- Four organisations.

- Yes.

- The organisation?

- The organisation.

- The organisations where information is held.

- So I envisage an information lens just so that clarifies where the information is held, where the gaps are that need to be developed over time, who's doing what with that information to a level without getting too wordy and then the, what are the key risks that need to be managed?  How are they managed and if they're not, what's going to be done to help make them managed?  So it can inform any policy setting that is required in the future.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- What use would HDC make of the White Paper?  What will it do with it or what's the next step?

- I think all of the agencies, as we work through this, it might require, if there's some new learnings or changes, it might require some additional work from ourselves to consider.  It potentially at a wider HDC view might have effects on district planning provisions around land use and the likes.

JUSTICE STEVENS:

- Or impact on systems within the relevant organisations?

- Yes, and it might see consolidation of systems.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- But you do need to end up, don’t you, with the best possible knowledge of the aquifer and how it can affect drinking water?

- Yes.

- Is there going to be a report on that?  Is a hydrogeologist going to be involved?

- So as I mentioned before, building on the massive amount of work that the hydrogeologists have already done, one element of the modelling that the Hawkes Bay Regional Council are working through with GNS and others is also the contaminant modelling element of that work and so that’s in its infancy and that’s a particular interest to the joint working group because the hydrogeology is one part but the ability for contaminant transfer is of critical…

- All right.  Coming back to the joint working group, in your view, what should it be in future?  What should its purpose be or purposes?  If you had a clean sheet, what would you make the elements of the JWG’s purpose?

- I think it can be a lot of things and my mind has actually jumped around to a lot of different things.  Under the current constructs that we have, because obviously if some of the constructs change with a water regulator or other elements, then the role of joint working group could change and clarity of, I mean as has already been mentioned, clarity of governance and direction is a key because the joint working group could end up being so wide that it achieves nothing.  I believe it needs to be more than a technical liaison group.  It needs to have set topics that are of key interest to the wider group that is focused on and works through from a drinking water perspective and collective results are reported and the agencies can then use those.  So it is around a collective group of individuals from each of the organisation, working on specific and shared issues in the drinking water realm.  It will move on what it needs to focus on.

- Well today, what are the issues it should be looking of most direct, importance to safety?

- The aquifer matters and understanding those wider risks and understanding.  This region comes from a place where deeply entrenched in the psyche is the pristine aquifer matters.  Our learnings highlight it is more variable than was historically believed.  We need to understand that more to change that learnings, if appropriate to understand where the risks lie.

JUSTICE STEVENS:

- And it is going to have a flow-on impact on public perceptions, public knowledge and public understanding isn’t it?

- Yes.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Have you experienced any problems or deficiencies in the JWG in your time in sitting on it?

- As I mentioned earlier.  The earlier part of it was very transactional.  I think the element that we are working through, finding the edges and having some governance clarity is when it is getting down to some of that specific consenting and keeping the autonomy of the agencies to be able to do the consent process clearly.  So how the nature I suppose of discussions happen.  We have struggled a little bit in that space but that comes with time as well.

QUESTIONS FROM THE PANEL: DR POUTASI

- Just one clarificatory but we might be able to pick it up with Mr Jones or Mr Wood.  So you are actually saying that the Ministry has changed its advice or its guidelines on boil water notices?

- So the wording with the rolling boil and the one minute is the advice we work with the DHB which was my understanding, the advice they got from the Ministry of Health.

- Do you know if they have formally published a change?

- I’m not aware.  The notice is as it was made for Waimarama and that was working it through with the DHB staff who were following is my understanding.

- Are aware of the formal publication of the guidelines.

- Yes.

- Which actually refer to the World Health Organisation rolling water for boil.

- Yes.

- I will pick it up again later thank you very much.

QUESTIONS ARISING – mr wilson – NIL

QUESTIONS FROM THE PANEL: JUSTICE STEVENS

- I just have one question.  Do you have the recommendations at page 157 of the Stage 1 report Mr Thew, have you got a copy?  These are the recommendations – thank you Ms Casey.

- Oh, yes.

- Do you see recommendation C?  The Water Safety Joint Working Group members notify each other and keep each other informed of any information that could affect drinking water safety risks?

- Yes.

- And then D, the Joint Working Group investigate aquifer matters of potential relevant to drinking water safety over the next 12 months?

- Yes.

- Now in essence the work that has been done in the White paper picks up elements of both of those recommendations?

- Absolutely.  C is also very operational so it is the agreement to share if an event happens, that the group is made fully aware of any incident.

- I am wondering whether given where we have reached, some clarification of those recommendations might be useful just to put a sharper focus on the work that is being done in the White paper.  I mean, for example, counsel assisting has drawn our attention to investigating aquifer matters having a hydro geological content and that isn’t all that clear from those recommendations, is it?

- Hydro geological input is a key element that we had implied.

- But you agree that some clarification might be useful?

- Yes.

mr gedye ADDRESSES JUSTICE STEVENS:

Just arising out of that, could I follow up with a couple of questions Sir.  When you are finished?

JUSTICE STEVENS ADDRESSES MR GEDYE:

No I am done.  It just seemed to me that we could usefully deal with this as part of the work on any variations to trhe recommendations after we have heard from Mr Palmer and Mr Maxwell because these were done last December in the heat of a hearing and work that was then being done.  We are now six months down the track.  You have made the very fair point that a lot of the work of the Joint Working Group was transactional, I appreciate that.  Part of the agenda that remains is important and I can understand that the work of identifying where information sits within four organisations, what overlaps exist, could it be shared better, is all really, really useful.  Let us put some time limits around that so that if it is useful to Stage 2, we get the benefit of it to the extent that parts of this work are ongoing.  Let’s identify those and separate them out.

QUESTIONS ARISING:  mr gedye

- Well I wanted to ask about recommendation E while we are at it.  This was a recommendation the JWG investigate the reticulation system.  It has been suggested by some that this is not really an appropriate matter for the JWG because it is HDC’s infrastructure and HDC controls it and it doesn’t really have any inter-agency overlap.  Do you have a view on whether the reticulation investigation should stay in the JWG?

- So this is one that the group has struggled with and it is a sort of a question that we have put to them and we understand that because there is no point myself or Mr Chapman or another member of my staff coming along saying, it’s okay, don’t worry about it.  That wouldn’t meet any test.  So we’ve talked through different ways of approaching that.  Whether we bring through one of the auditors and to be fair to the other members, it is not in their normal realm of understanding or their work focus, so it is very difficult for them to be able to a strong landing apart from asking sort of small overview governance questions.    So my view is it doesn’t sit naturally in that space.  There is absolutely a discussion between the Drinking Water Assessors and ourselves.  They have an overview interest to make sure that the reticulation is not creating safety issues.  So I think it creates more of a distraction to where the Joint Working Group could focus on.

QUESTIONS FROM THE PANEL CONTINUES: JUSTICE STEVENS

- Now could I just ask a follow up.  Is that investigation into the retic and distribution systems, one of the aspects of Dr Deere’s work?

- So that is where the Joint Working Group got to around getting advice from Dr Deere on that perspective at a higher level.

- So you, on behalf of HDC, wouldn’t have any objection if a variation of this recommendation was that it be taken out of the responsibility of the Joint Working Group and sit where it probably ought to sit, namely with the water supplier?

- Yes I would have no issue with that.

- And that the relevant work covered by E, would be dealt with, with advice from Dr Deere?

QUESTIONS FROM THE PANEL:  MR WILSON

- I have a question on that regard.  Section 69 ZZZ I think, Z of the Health Act requires the water supplier to have an effective back flow regime.  I am not aware that that has ever been audited anywhere in New Zealand as part of compliance of drinking water on an annual basis.  There is a recognition that back flow does represent a risk to this network, probably more so in the Havelock North area than the Hastings area because of the elevation issues associated and the risks of banks opening.  Have you given any thought about how you might jointly work with the Drinking Water Assessor to be able to demonstrate that you have met that obligation under the legislation, on a regular basis, possibly annually?

- That is thank you Mr Wilson, a topic we want to carry on.  We have been doing just some pre-work on that.  We organised a local workshop where we bought in – sorry I forget the chap’s name from Tauranga, around the backflow with our Building Act, our building officers and officers from central Hawke’s Bay.  Unfortunately Napier were in their event so they weren’t able to attend.  So just working out, getting collective learnings, pulling that together, working out how do we design a better way to demonstrate and work through that.  Carly Price, discussions with her the other day, we were having those and talking through some of her experiences and the approach in New South Wales, how they were approaching that issue as well.

- Because it occurs to me that that is the one area of reticulation management that does have an overlap with one of the members of the Joint Working Group in that it does have an overlap with the regulator because you have a legislative obligation?

- Yes.

JUSTICE STEVENS:

Well that is covered in an amended recommendation

QUESTIONS ARISING CONTINUES:  mr gedye

- Finally just an afterthought while I have got you.  The laboratory issue.  Can I just ask you in terms of safety today.    Are you satisfied that the laboratory or laboratories of HDC is using, up to scratch and performing well?

- For everything that I have seen and the nature of the discussions I have had and I am not a microbiologist but we do have Dr Deere going to visit them, either today or tomorrow, once we can release him.  I have nothing in my mind that would raise any significant concerns.  We are keeping a clear eye on them and they are very aware of that and I guess the key piece of my concern with them and the discussion with them is around capacity, making sure they maintain enough capacity so processes don’t trip over when they get busy.  Just acknowledging, they are starting to pick up more of the local regions work so capacity is one we are watching to make sure that they are fully geared up to be able to deliver on all of their requirements.

FURTHER QUESTIONS FROM THE PANEL: JUSTICE STEVENS:

- For example if, if that the outcome of a variation of the recommendations was that increased levels of testing, sampling and testing were to occur following periods of heavy rainfall or a water event, as defined, then that hey had the capacity to deal with it.

- Yes we would have to have a plan and that they might mean that we would have to use some staff who are suitably trained to do the testing to supplement but we need to work through that discussion around how would you actually deliver that.  What happens if they have a level of sickness, so you have got a contingency plan on the testing as well.

- Well and I am thinking if a rain event were wide spread and other areas were making similar demands, either as a result of the work of this Inquiry or howsoever, that there was not just capacity with that provider, but also access to another accredited laboratory, that is able to perform?

- Yes and I think that is all of the elements thinking through an events based response monitoring, is understanding what sort of events, how widespread it could be, what is the implications, when if that event happens because you could design something that you actually can’t deliver on as well.

- Because the providers can’t provide?

- Yes because obviously it takes a local resource to be able to go and collect the sample.  Once you have got the sample then there are a number of laboratories who can test the sample and as was traversed through Stage 1, there were some issues in a lab in a different area historically as well.

- Which of course puts the spotlight on the discussion we had yesterday about making sure that the Ministry of Health are fully informed of –

- Yes.

- – what went wrong.

- Yes.

- So those letters will be written won't they that we talked about?

- Yes, they can be re-written, they can be written.

- Yes.

- Yes.

QUESTIONS ARISING continues:  Mr Gedye

- Well, when you say “re-written,” you haven't yet written to the Minister of Health –

- No, so –

- – Ministry of Health, have you, about ARL Laboratory?

- No, the letter went from the Drinking Water Assessors to the Ministry of Health rather than directly from ourselves.

- Well, from your point of view, is there any reason why you shouldn't register your concern as well as the supplier?

- No.  We traversed that yesterday and I agree that was an idea.  I think at the end of the day, there was a – you don’t need to, but we can write a letter.

JUSTICE STEVENS:

- Well, what happened at the end of the day had nothing to do with the points that the Panel were making to your organisation as a contracting party to a contract that had failed to deliver.

- Understand.

- The reason for the failure needs to be explained to the body that has responsibility for the regulation of the laboratories.

- Understand.

QUESTIONS ARISING: Ms ridder – NIL

QUESTIONS ARISING: Mr Matheson – NIL

QUESTIONS ARISING:  Ms butler

- Mr Thew, I am counsel for the Department of Internal Affairs.  You mentioned section 17A of the Local Government Act to do with service delivery obligations.  Is this the first time that you will have reviewed – that you have applied those section 17A obligations to review service delivery for water supply?

- Yes, so Council is working through a full programme of section 17A reviews as per the Act.  Initially prior to August event, because of the nature of the contract with City Care, there was an ability to do the section 17 review of the water services a little later under one of the exclusion clauses; however, we were going to do it recently this would have started and it was in my programme of works in September, but obviously events of August re-changed my priorities and work programme quite significantly and the resource I have brought in to help me out is leading that, so for water services, yes, this is the first section 17A under that format review.

- So the change – so that work that you have just described and the change process will be complying with section 17A?

- Yes and so Bruce Robinson is leading that on my behalf.

QUESTIONS ARISING:  Ms casey

- Mr Thew, there is just a few aspects from your evidence that I would like to unpick a bit further and I am starting by taking you back to as far as yesterday and early in the day, counsel assisting was asking you a question about Brookvale bore 3 and the question that was put to you was along the lines that there were no technical or infrastructure reasons why BV3 couldn't supply the whole area and I don’t think you quite got to finish your answer about the constraints on that proposal in terms of environmental effect, so I just wanted to step back to that and explore that a bit further?

- Sorry, just moving my brain back.  The – so I think –

JUSTICE STEVENS:

“Whole area” you mean Havelock North, is that right?

QUESTIONS ARISING CONTINUES:  Ms Casey

- I think that was the question that was directed to.

- Yeah, so if I recall the question was around was there a technical or any other reason why we couldn't supply all of it from Brookvale.  There were some technical elements just around creating enough pumping capacity, which is not so difficult.  The other element though is working through the assessment of effects, both hydrologically, making sure we're not creating negative effects on other parties but also continuing the discussions with Ngāti Kahungunu, who are a key part of that process that we need to work through to understand their concerns, any issues and to make sure any application, not only of that view of the Brookvale but our wider strategy in other locations to get their inputs as part of our thought process and development, yeah.

FURTHER QUESTIONS ARISING FROM THE panel:  Mr Wilson

- So, Mr Thew, just to follow up on that, as I understand it from what you said yesterday, it has been clearly demonstrated that abstracts from Brookvale 1 and Brookvale 2 had an adverse effect on the flow of the Mangateretere Stream but that it had never been conclusively demonstrated that operating Brookvale 3 had the same effect on the Mangateretere.  Is that what I heard you to say yesterday?

- Yes, that’s the technical element but we need to work through that discussion with Ngāti Kahungunu and make sure we've understood the wider cultural perspectives into that as well.

- And I also heard you say that there were what I would describe as community perception issues about the continued use of Brookvale 3.

- That is correct.

- Because of the history of contamination from the Brookvale area generally?

- Yes.  So because obviously the event and the branding of Brookvale for water sources is fairly well etched, and also the perspective of how we drink water in the Hawkes Bay has always been it's come out of the ground and you can drink it directly and what the current context of Brookvale is, it's not that at all.  We're treating it as though it's a water source that’s gone through a large filtration bed to strip the dirt out of.

- Just following through on this, and I am sort of plugging on my theme of yesterday from around strategy, so there is a desire for a number of reasons that we should not use Brookvale 3 and there is uncertainty as to whether it might impact on the Mangateretere.  That is a fair assumption of where we have got to in those two questions?

- Mangateretere, from the technical advice I have, is it's highly unlikely an effect but absolutely around the perceptions is it is something to work through.

FURTHER QUESTIONS ARISING FROM THE PANEL:  justice stevens

- And presumably, you would add into the mix the potential risks from the compromised aquitard at TMM, Te Mata Mushrooms?

- Yes.  So that aquifer being highly leaky and so by us taking that catchment as a surface water, the key concern in and around any areas where surface water can make its way through is chemicals.  That’s the key concern because we are treating it as a surface water.

- That is the context?

- Yes.

- That Mr Wilson is putting.

FURTHER QUESTIONS ARISING FROM THE PANEL:  Mr Wilson

- So taking the strategy discussion a wee bit further, historically that Havelock North supply – well, until recently, the Havelock North supply has tended to be operated as a separate supply from the Hastings supply partly for historic reasons and partly because of the size of the infrastructure connecting the two, is that correct?

- Correct.

- Okay.  And I also heard you say yesterday that there was a desire from a resilience perspective to have a source on that side of the broader network, for want of a better description, if you were to treat the Hastings and the Havelock North.  So that drives me to two questions.  One is, looking in the future, what are the advantages and disadvantages, and I am not expecting you to answer this but I am just sort of going through a thought process in terms of defining strategy.  You would then ask yourself what are the advantages and disadvantages of continuing to operate them as separate networks versus operating them as an integrated network?  If you were to operate them as an integrated network, and you did achieve a source on that side of the broader network that provides resilience to both networks, so there is advantages of doing so and as you had discovered over the last 10 months, there is advantages of operating in the opposite direction.  There is nothing quite like a bit of resilience in a network.  So that would drive me to suggesting that operating them as a broader network makes sense from a resilience perspective and from an operations perspective.  It then drives you to a simple question, which is, how important is a source on that side of the network because you could achieve that resilience in another way.  You could achieve it by running a highly resilient ductile pipe network out there.  That is not unknown.  So it comes down to when you are developing strategy, you really just need to drive some stakes into the ground quite early on.  It strikes me that the big strategic decision that Hastings District Council have got to make, pretty damned quickly, is what is the future of BV3.  I just wondered, do you have a timetable for making that decision?

- So all your points are absolutely valid and that’s almost like you were sitting in the discussion with Mr Cousins and Ms Sweeney and Mr Chapman and myself.  In terms of timeframe, as I said yesterday, I just need to go back and just check that there was some additional work to help inform that absolute yes/no discussion.

- We would love to know –

- It's very shortly.

- We would love to hear the conclusion to your debate in August.

- Yes.  That was well and truly understood from yesterday.

- Thank you.

QUESTIONS ARISING CONTINUES:  Ms Casey

- Thank you.  Your reference to the HDC’s water supplier taking that catchment, the Brookvale catchment as surface water actually leads to the next area I just want to clarify some of the questions and answers that we went through yesterday.  So counsel assisting took you through a number of issues relating to the Brookvale Bore 3 and I at least got the sense that there was a suggestion that Council wasn’t moving fast enough, there were a number of questions or surely this issue should have been resolved with urgency or that it was urgent that such and such an issue was resolved.  I just want to step through some of those and talk to you about why Council thinks that – why the HDC thinks that these are important issues but not necessarily urgent issues from water safety perspective and that’s the point that I wish to clarify today.  Of course they are important in terms of understanding your catchment.  So first of all, when you say you're treating that catchment as surface water and there's been references to the log 5 treatment, can you describe the level of contamination or in layman’s terms, how clean or unclean raw water is, can be treated by that log 5 treatment to turn it into safe drinking water, just in very broad terms?

- So the log 5 treatment is, just trying to think how to do this simply without getting into a complex water treatment discussion.  So I think probably using the analogies, if I put chemicals aside, because the nature of treatment won't deal with chemicals and the supply source we're using the ground to scrub the dirt out, that makes very low tepidity, is we could treat the water that’s out of the Tukituki would be an analogy.  So I talked about yesterday I understand the Waikato River in parts, if I put chemicals aside 'cos it's a completely different problem, requires a 3-log treatment for bacteriological and pathogenic treatment.  So in terms of the logs, it would turn 100,000 bugs to one.

- So when you say we could treat the Tukituki, are you saying that if you applied the treatment you currently have at Brookvale 3 to water from the Tukituki, it would be safe to drink?

- Yes.

- So none of the issues that Council raised about catchment and aquifer safety raise any current issues with drinking water safety in terms of the water that is being supplied from the Brookvale Bore at the moment in light of your treatment?

- No.   So they’re areas of interest to understand what is going on in the catchment, but the way that we are operating it based on the modelling of Mr Cussins, we are taking that potential risk and operating as though that risk exists and so we’ve assumed the worst-case scenario in the operation.  The key piece in that catchment survey, I believe, was at the time of the survey there was some treated timber stored within the catchment.  That was, that's probably the key risk within that catchment because the plant wouldn't treat if there were – if someone started a business that wanted to treat timber in that catchment, I would be having –

- A different problem, right.

- – a different problem and there would be a very vocal discussion around land use.

- So just to get this very clear, you are already treating the water on the basis that the aquifer has been breached?

- Correct.

- So while it's important for you –

JUSTICE STEVENS:

- Surface water.

- Yes.

Ms Casey:

Yes, I am just wanting, just because of the – some of the questions that were asked yesterday, I just wanted to make that very clear.

JUSTICE STEVENS:

We understand.

QUESTIONS ARISING CONTINUES:  Ms Casey

- So while the resolution of whether the aquitard has been breached is important for your knowledge, it wouldn't change the treatment that is currently been given to the water to make it safe.

- No, no.

MR WILSON:

With again the notable exception that you commented before that a breach in the aquitard that close to the source does expose you in the event of a chemical spill

QUESTIONS ARISING CONTINUES:  Ms Casey

- Absolutely so – and I think we’re putting that risk to one side at the moment because that’s a future planning issue.  So I just want to take – so the fact that there are cows near the bore head, or a number of coliforms in the water, is not affecting – posing any risk to the current safety of the drinking water in light of the treatment you have in place?

- So with livestock in the paddocks or some total coliforms coming through, the treatment is in extreme excess to deal with that, the expected levels or the potential levels.

- So and that would be the same for the number or the results of Protozoa tests in the raw water or the age of the water?

- So the process is designed to remove Protozoa should that occur.  The testing to date hasn’t shown any but that’s not to say it can't happen so that’s why the treatment is designed to remove the Protozoa should they happen.

- And similarly, is that the same issue with the Te Mata Mushrooms investigations and the like, you're treating the water on the assumption that those investigations bring up a negative or a worst case scenario?

- So based on the current operation and the understanding from the modelling work of Tonkin and Taylor, we're treating that on the worst case scenario of the current operation.

- Thank you.  Now, just one more topic I want to touch on.  There was a discussion yesterday about some analysis of samples that Dr Fricker had looked at and there was a reference to 126 samples and there's been some exchange this morning to talk about where that reference of 126 high readings came from.  Is there anything that you'd like to talk about in terms of samples that Dr Fricker was working from?  I’m not sure if you’ve had a chance to look at that exchange this morning.

- So yes, I sent a reply back.  Without looking at the raw data, and just at the note that was forwarded through, I believe Dr Fricker was looking at a wider dataset across all the supplies so it was picking up some of the readings through the Esk and the Waimarama as different areas and also looking back through the events of August and the like, but without actually sitting down and either talking to him or looking at it, I haven't analysed further.  I did recheck my numbers last night so, in my report, so from results of the total two litre total coliforms from 1st of January, I just double-checked that I hadn't made a mistake so the 32 across the bores over that period is the number on the worksheet on the supply and I also have it broken down just around how, what months.  I can share with the Panel we had a forecast for a potential high rainfall so we did instigate the higher frequency monitoring at Brookvale over the weekend.  So we had multiple tests per day.  All those two litres came back as absence for both total coliforms and for E. coli.  We will watch for the next few days because the work that Tonkin and Taylor had highlighted a potential lag, so that will be very interesting because as I said yesterday, it takes a series of data points to truly see trends rather than just random coincidences.

FURTHER QUESTIONS ARISING FROM THE PANEL:  justice stevens

- Just to help us with some possible work around heavy rainfall event, what was predicted?

- I can't recall what the predicted rainfall actually was.  The team came to me and said there's a potential for high rain.  We don’t want to make the decision in the weekend.  Should we just go now.  So I'd have to check what the forecast was, Sir.

- Okay.  Because that is an area that I think could usefully be included in any amendments to the recommendations.

- Yes.

- And I think you picked that up from yesterday but any work that you and your Council can do to assist on that would be much appreciated.

QUESTIONS ARISING CONTINUES:  Ms Casey

- Yes, those comments have been taken on board and I think already identified in terms of the discussions between experts and discussion about where Dr Fricker and Dr Deere are both converging on that very same point I think.  So that is well underway.  Just while we're on the topic of Dr Fricker’s comments, you will have seen some of his comments expressing quite strong surprise at some of the results and perhaps informal comments suggesting that the HDC might not have been following proper processes.  The example that springs to mind is one that counsel assisting touched on yesterday in terms of the 10 transgressions.  From your reading of his comments, could you tell whether Dr Fricker was up to speed on what HDC has been doing with its monitoring results?

- I think it's difficult for me to answer from just reading what I've received.  I think my take on what I read is he's made many assumptions without understanding what is going on, on a daily basis and I think that’s, I guess, a difficulty he has without being able to have a discussion or see the greater depth around not just the raw numbers but the context in which they're operated in, the work that goes around and actually what response did and did not happen.  So I think it's very difficult to just look at raw data without actually – and then joining assumptions.  It's, you need to understand the whole situations otherwise you can jump to the wrong conclusions.

- I think one of the issues that came up yesterday was from what you'd seen did he know anything about the HDC’s response to those three events and the 10 transgressions.

- I do not believe so.

JUSTICE STEVENS TO MS CASEY:

- He cannot answer that question in the sense of what Dr Fricker’s knowledge was.

- No, Sir.  I think the concern that I'm just trying to flag broadly is that a number of –

- I understand the flag.

- Thank you, Sir.

- And the answer is that there is nothing to stop Dr Deere talking to Dr Fricker.

- Sir, it's not about consultation with the experts.  It's more a concern with a number of assumptions that seem to have been made in the last few documents suggesting that proper processes were not being followed when it was reasonably apparent that Dr Fricker, and indeed why should he be, was not across the processes for responding to those transgressions.  It was not –

- I do not think we can make assumptions either way and we are not going to.

- Sir, I've raised the flag for the Panel that we have some concerns about his level – the basis for some of the adverse comments that were made.

- Yes.  Well, to the extent that that happens, it seems to me there is absolutely no reason why Dr Deere cannot pick up the phone and have a talk to him.

- Well, that’s a very helpful indication from the Panel and one that I'm sure the Council will –

- We had an extremely successful science caucus where the Panel is delighted that Dr Deere is being retained and we are now going to hear from him.  So I do not know that this is all that productive.

- That’s fine.  Thank you, Sir.  In fact that was as far as I wished to take that point and I just have one more question for Mr Thew.

QUESTIONS ARISING CONTINUES:  Ms Casey

- So we're talking – I'm now moving to the issue of the water safety plan and there's been a lot of discussion about the usefulness of the process control chart and I think everybody is on the same page of that but one element that I wasn’t sure was clear in the interchange was, am I correct, and tell me if I'm not, that the process control chart that you're talking about is not just a simple one-page summary of existing content but is this a much more fulsome approach that takes a different approach to risk management and assessment, that will lead to this process control chart?

- I think the detail of that question, Dr Deere would be far better to get through but it is around highlighting the need to move to managing and that control point process, so it is far more apparent.

- So it is not just a visual executive summary that could be done with ease?

- No but I mean it does summarise some of those processes into a table.  It is not one table or one box but it is not nearly as lengthy and detailed as the risk tables at the back of the Water Safety Plan which you wouldn’t expect someone who has nothing to do with that or a governance or an executive people to wade their way through and find a meaningful picture.

- Thank you.  That was the last point I wanted to clarify.

JUSTICE STEVENS ADDRESSES MS CASEY:

I think Ms Casey what we have in mind and this is something we can tease out with Dr Deere, is something that says, in the event of a contamination occurring, Mr X will be responsible, is the responsible officer.  In the event that Mr X is at a conference or away from work or unavailable, Mr Y or Ms Y will deal with it.

MS CASEY:

Thank you Sir.  That was actually the point of my question because I think, if I have understood things correctly, that there has been a slight talking across – that as understood that this is what the Panel is looking for and I think the Panel may have been getting a little frustrated at the responses you were getting about the complexity of developing a control point process focus.

JUSTICE STEVENS:

Not necessarily.  We understand that behind any product there will be a process.  Dr Deere has come up with a bow tie model, fine we will hear about it.  But output needs to be something that can be fitted on to one or two pages, executive summary right at the very front.  Because it is the multiple audience about which Mr Thew spoke, can pick it up, open the first page and say, oh Mr X is in charge and in event he is away, someone else is and these are the steps that you follow, 1, 2, 3 to 10.  Okay?

MS CASEY:

Yes absolutely.  I have no further questions.

JUSTICE STEVENS:

Thank you Mr Thew and good luck with your ongoing endeavours and hopefully there has been some food for thought.

WITNESS EXCUSED

MR GEDYE CALLS

DANIEL DEERE (AFFIRMED)

JUSTICE STEVENS:

- Good morning Dr Deere.  Welcome and make yourself comfortable.

- Thank you.

CROSS-EXAMINATION:  mr gedye

- Dr Deere I would like to first deal with the highest level about the water safety of the Havelock North supply.  How long have you been involved in advising the Council now?

- So I first came to Council in April and the first contacts I had from Council as I recall were around February this year.

- So have you had time to get a reasonable overview of the water supply system?

- Yes I have. So I have been out with the operators to all of the current production bores, all the bores that are used.  Had a look at some of the areas in the immediate surrounds of those bores and also met with various people including a Drinking Water Assessor, Dr Fricker, some of the Tonkin & Taylor personnel and discussed with those personnel and also to the local laboratory and the Palmerston Laboratory that does the Protozoa testing.

- If one is looking at the current and future safety of the water supply in this region, am I right that it would be desirable to have a strategy, an overall plan?

- Correct, and that would be ordinarily captured in the water safety plan as the main purpose of the water safety plan is to bring together that strategy.

- Would you accept that the current version of the plan doesn’t yet represent a holistic strategy or all strands of a strategy?

- When I first saw the water safety plan, the main concern I had was that it was lacking the extract that provides the operational day-to-day control information that’s required.  It did have the risk information table that was required.  It covered types of risks that needed to be managed and the preventive measures that were in place as required in the Drinking Water Standards and the guidance that goes with those Standards but it was lacking that operational part, so in that sense, it was more of a management-level academic-level document and it lacked the bit that the operational, operations needed and so my view was that is that I'm a drinking water auditor for a lot of regulators and I said that in most jurisdictions that would not be deemed a compliant water safety plan but in New Zealand it would because in New Zealand the regulations don’t require that level of detail and so therefore on a global scale, as the professional in water safety, I would say it isn't adequate but it is adequate in terms of meeting the local regulations.

MR WILSON:

- So it is not best practice, would be the easiest way to summarise what you have just said?

- Correct.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Can I come back to high level strategy.  Do you consider that Hastings District Council has, and leave aside the water plan itself, do you consider it has a sufficient strategy or vision or plan for the things it needs to do to have a high-quality safe water supply system?

- I've only looked at the more operational level so I wouldn't know if there is a long-term strategy.  They had been focused, in the sessions I've had with them, on the immediate need to manage the immediate risks, which makes sense under the circumstances but I couldn't comment on a five/10 year-type strategy.  I know that – I can see the kind of thing you're envisaging, which would be, and I often see these sort of five/10 year-type plans, I don’t know if Council has that sort of strategy.  I couldn't comment on that.

JUSTICE STEVENS:

- Just pausing there.  You have obviously heard the exchanges, particularly –

- Yes.

- – that Mr Wilson had with both Mr McLeod and Mr Thew?

- Correct.

- About for example what is going to happen with BV3.

- Yes.

- And having a dedicated supply on the Havelock North side of town.

- Yes.

- Those sorts of discussions and I think that is the area that counsel assisting is interested in gauging your involvement in or understanding of, that type of five to 10 year strategy.

- I've not probed, I've not tested that.  My reading is that there are still some questions being answered about what type of treatment, what type of system might be put in place.  There are contracts to be let to construct assets and so on, so I don’t know if there is such a strategy.  I couldn't answer that.

- Because ideally, before you start, I mean we heard yesterday, $12,000,000 approximately allocated in terms of asset acquisition.

- Yes.

- Before you start investing those sorts of sums, you would want to have a strategy would you not?

- And I think my biggest concern there is about, with the Inquiry taking place and the media and publicity, is that Council is getting a lot of recommendations and a lot of actions, so what I've been trying to, in my mind, to see how I can advise Council is trying to set the priorities, what are the most of those intentions and that advice I think would go into some broader strategy but I haven't tried to look for that broader strategy.  No, I've not looked for that.  It would make sense to have one.

MR WILSON:

- But just following up on your point that it is very topical and there are a lot of submissions coming from every sector, there is a risk in that environment, is there not, that you end up with paralysis by analysis?

- Yeah.

- There are simply so many options out there that it is difficult to see the wood for the trees?

- Yes and also you may end up with over-engineering in one area at the expense of another as well.

- Mhm.

- So you could – you can end up with all kinds of adverse outcomes, I agree.

- Well, in fact, in a way we do have that in that we have, at the moment in Havelock North, a substantially higher level of treatment in Bore 3 than the water that is providing Havelock North from the Hastings sources?

- I would agree with that.  And that is understandable in the circumstances, but I would agree that would be considered an over-engineered barrier.

- Yes.

- In the current circumstances.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Well, would it be fair to summarise the situation by saying to have a durable and robust safety system, this might be a good time to step back and slow down and prioritise and plan?

- Agreed.  If the satisfaction, the immediate risks are managed, a more strategic approach would lead to a better outcome for the community.  I think there is pressure to be seen to be doing things, the pressure to do some things quickly and that may distract from that, but ideally there would be, as you say, a strategic plan to allow objective analysis, although I take the point about analysis paralysis as well.  There has got to be some timeframes on that.

- I’m not quite sure where your experience and skills start and stop.  Is strategic planning something you can contribute to, or is that outside what you do?

- I have not been involved in strategic planning when it comes to looking at prices, tendering, forming decisions on which contractor or consultant to go with.  My experience has only been really in advising on what the risks are and what level of control is required to manage the risks.  It's then others that will do the procurement of those things.

- Yes, that’s what I meant, that –

- No, I’m not involved in that.

- For example, there is a need, isn't there, in the Hastings bore fields to have quite a holistic view: should they all have UV, how many treatment plants should there be, should chlorination continue?  I take it you can contribute to all those sorts of issues?

- Correct, that’s the sort of thing so I do that kind of worth for other Health Departments where I am asked to advise Councils on exactly that sort of thing, but I don’t get involved in then the tendering or procurement of the –

JUSTICE STEVENS:

- Well, of the engineering and the purchasing and so on.

- Correct, yes.  And they like to keep that separate, I like to keep the engineering consultants, to avoid conflict of interest, separate from the health advisory personnel.

- I think it's the upstream rather than the downstream that we’re exploring whether you could value in terms of strategic advice.  I mean, you heard the discussion yesterday and you’ve told us about an over-engineered safety barrier with the treatment plant in Brookvale Road.  I mean, if and to the extent that Brookvale 3 were not going to be pursued –

- Mhm.

- – that adds a whole new dimension doesn’t it to the –

- Correct.

- – decision-making and the planning?

- Yes, absolutely.

- Yes.

- And in principle as part of your strategy you would look to use the lowest-risk bores –

- Yes.

- - over other bores and if that involved a few new pipelines you would accept that and there is one of the guiding principles on the first couple of pages of the Drinking Water Standards New Zealand is about risk minimisation and multiple barriers and the first barrier is to choose the best available source, for instance.

- Mhm.

- So that sort of strategic planning would be part of that.

Mr Gedye:

We’re going to move onto the Water Safety Plan if the panel has any other questions about strategy?

JUSTICE STEVENS:

I think – Dr Poutasi?

DR POUTASI:

I don’t.

JUSTICE STEVENS:

I think the indications are clear.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Dr Deere, tell us a little more about process control and what you think should be done to improve the water safety plan?

- Yes, so the first response I had when I first saw he Water Safety Plans was a surprise that process control summary that would be aimed at the operators of the treatment systems and the operators of the distribution system, that that wasn't attached or in some way part of the Water Safety Plan and it was explained to me that the reason for that was it's not required in the Standard and I checked the most recent versions of the Standard, the 2016 Water Body Management Guidelines, the 2014 versions of the Public Health Risk Management Plan templates, and I was surprised they were still written as they were in 2001 which was written at a time when Water Safety Plans were new and the focus then was on having a risk information table that summarised the risks and summarised the preventive measures and the focus then was about building new treatment plants and putting in barriers.  It wasn’t about operating them and since then, the industry’s moved on and the focus now is on operating those barriers correctly and ensuring, for example if you backflow prevention devices, that they are tested at a certain frequency or if you have a treatment plant, it's monitored at a certain frequency and that part was missing from the plan but it's not required under the Regulation.  The Regulation is still written around a list of risks, preventive measures and that improvement plan to add new preventive measures.  So I was, I sort of took back my criticisms and said okay, fair enough, you’ve met the Regulation but you haven't met what would be a good practice and my comment was that that would mean that water safety plan, I couldn't audit it operationally.  I would consider it wouldn't be a compliant water safety plan in comparable jurisdictions.

MR WILSON:

- So, Dr Deere, is it fair to say that not only do we have Drinking Water Standards which have not been substantially reviewed since 2005, we also have guidelines for water safety plans that have not been substantially reviewed since 2001?

- They’ve been – correct.  They’ve been updated and improved in terms of the scope and the number of examples but the underlying purpose of those guidelines from 2001 was to take the first step at a time when a first step was required.  The next step hasn’t been taken and I'm across this because in Melbourne when I was working at the time, these guidelines had been drafted, we were learning from the ESR and Ministry of Health staff, they were visiting us and helping us set up a framework in Melbourne.  The World Health Organisation was learning from New Zealand Ministry of Health and ESR and they flew them out to Berlin to a big meeting on water safety plans and at the time, it was recognised as world-leading practice but it hasn’t evolved and so it –

JUSTICE STEVENS:

- It got stuck?

- Yeah, it's got stuck and because it was so good at the time, I guess there was a sense of this is good practice and it was best practice, it was leading practice at the time globally but it hasn’t gone the next step and the lesson we've learned with water safety plans is that it's all very well having a nice big technically correct academic document that describes your risks but what happens day-to-day when someone fixes a burst water main and the day-to-day activities that occur operating a treatment plant, that’s what actually manages the risk.  So the water safety plan has to spit out some kind of concise auditable reportable process control summary and the parallels are in other industries, the food industry, pharmaceutical industry, farm production industries and quality assurance.  The parallels in other industries as well.  It's not different from those situations and that’s the gap.  The water safety plan is still too theoretical under the current framework.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- But HDC is agreeable to insert the process control and you're going to help them with it?

- Correct.  So my view is that was the first priority is to do that.  It's easy.  It would take less than a day to write a process control summary for water supply.  The problem, the part that takes time is it needs to be done with and have the ownership of the operators because it has to reflect the real world.  It has to reflect what's actually happening, what the water authority can actually do.  So we may say academically you should measure something twice a day and they may say we can't do that.  It's going to be once a week and we are writing the water safety plan.  It's done once a week and have an improvement to improve that because water safety plans should be auditable and I should be able to look for records to prove that in fact the operator was doing that thing once a week as the water safety plan states it.  So that’s why it has to be done with the operators and have the ownership and their full understanding.

JUSTICE STEVENS:

- Now, what you would do will reflect the current practice in Melbourne, is that correct?

- So what we would do would reflect the current practice in terms of the operational practice here but the standards it would achieve would be, I'd be using the World Health Organisation model of water safety plan as a template as the global norm that is applied in Melbourne, Sydney, supplied in the UK, supplied in Canada, wherever else water safety plans are used, China for instance and South Asia as well but would use WHO as the global norm, bearing in mind the WHO heavily drew on the New Zealand standards for its template.  So it's 90% the same as the current Regulation.  It's missing that operational part.

- And it has moved on as you said?

- Yes.

MR WILSON:

- And when you say, you will reflect what happens here.  That is just the reality that you must reflect what happens here because there is no sense in having a plan that says, the operator goes there weekly when in fact he goes there monthly?

- Correct and that would then lead to, in the context that I am familiar with, where Water Safety Plans are usually required under regulation, the assessor, the Drinking Water Assessor or equivalent would be asking for evidence, that the operator is following the Water Safety Plan so there is no point in writing one if they are not following.

- No and that evidence would be a record of their visit weekly, by way of example?

- Yes.  It would be log books, it would be electronic data records, it will be laboratory records, those types of things, photographs.  Whatever is chosen as the record keeping method to prove and those records will be considered to be of legal significance.  They would be records that the operator would have to produce in an inquiry like this to show that they were following the Water Safety Plan.

- An indeed the Health Act requires water supplies to maintain records?

- Yes and that is the same thing in other production industries.  You know the food industry, if you go to the local McDonalds, there will be records in that McDonalds about how they check the heaters are at the correct temperature, the fridges are the correct temperature, it is the same concept.  It is nothing that is difficult to understand or utilise.

JUSTICE STEVENS:

We will just take a 15 minute break and resume at 11.15 and look forward to discussing these developments with you.

INQUIRY ADJOURNS:	11.00 am

INQUIRY RESUMES:	11.15 am

WITNESS ON FORMER OATH

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Dr Deere just before we leave the Water Safety Plan topic, we will in the August hearing be examining whether the New Zealand Guidelines for Water Safety Plan should be changed.  Are you able to point us to the best exemplar of what a prescription for a Water Safety Plan should look like?   Is it a WHO document or is it an Australian document?

- The global point of departure which is a term that I use, a term the World Health Organisation uses, is a Water Safety Plan portal that the World Health Organisation and international water association maintain and it has got the World Health Organisation’s various iterations of the Water Safety Plan.  You can see how it has changed over the years and a huge range of training processes, a training package, a training of trainer package for trainers and case studies and examples and then a whole suit of detailed texts.  So Water Safety Plans for building, treatment plants, surface waters, groundwaters, distribution systems that go into detail and how you apply Water Safety Plan details contexts.  There is other jurisdictions that have their own versions but they tend to be flavoured by the local politics.  WHO one is probably the most pure one and it is contributed to by all those agencies so I would use a WHO WSP portal as the place to start.

MR WILSON:

- So Dr Deere, how much local customisation is necessary.

- Not a huge.  Not a huge, but there are usually, for example, different jargon terms used.  A good example is the term Water Safety Plan.  In some countries, Water Safety Plan is used in swimming pool safety for recreational water safety and Australia is one of those countries so they are not called Water Safety Plans in Australia because that is confused in the environmental health officers mind with the drowning control plans in public pools.  So the term Drinking Water Quality Management Plan is used in that context, so there is little things like that.  Other jargon terms are used but it is normally that sort of flavour, or they can be local standards that you want to refer to that already cover something, that would otherwise a Water Safety Plan.  So for example the plumbing regulation and plumbing code, largely covers things like back flow prevention.  It may simply just refer to the Plumbing Regulation rather than talk about a Water Safety Plan for a building.

- And what about geologic situations.  New Zealand has, as you are probably aware, a number of geothermal waters which represent chemical contamination risks.  Are those adequately discussed in the generic framework?  Would you need to customise them for something as specific as that?

- There's a groundwater monograph that WHO has as part of its water safety plan package.  I don’t know whether or not it would cover some special cases and there could be special cases but generally speaking, WHO tries to capture those.  So it probably has but I don’t know.  We’d have to check.  So for example, in Northern Australia we had big problems with the mining towns that have very long pipes.  They have above ground, the groundwater can be geothermal.  It can be ambient temperature but it gets piped in huge above ground pipes, gets very hot, gets full of nasty pathogens that can kill you and that’s a special case but it is covered in the WSP guidance because somebody in Australia made sure it got in there.  Your special cases may or may not be in there.  There's been a lot of involvement from ESR and Ministry of Health with WHO over the years and so I suspect it's probably covered but it may not be.

MR WILSON:

- So would it be fair to say that it is not a large piece of work to ensure that if you took the latest best practice version, to ensure that (1), it aligns with New Zealand terminology and technical jargon, (2), that it aligns with the legislative and regulatory framework, particularly the parallel regulations, and (3), that it covers the unique or semi-unique climatic and geological conditions, that to check those three out is not a big piece of work?

- It's not and there are still people on the original committees who are well networked with WHO who in New Zealand that could do that work.  The only problem is the cost and not the cost of doing the work.  It's the cost implications for the industry.  So what holds back – what held back the original push for a more comprehensive water safety plan in New Zealand was pressure to avoid costs to the water sector and the same delays apply wherever anybody tries to apply water safety plans, so the technical part’s complete, relatively straightforward.  The problem then is people look at that and say, oh, I will now have to put in place, for example, online chlorination monitoring where I now test it once a week.  I've got to buy a point analyser.  I've got 45 bores.  It's going to cost me X dollars and if, what that means is they push back on it.  The political process, which involves a scientist, that can take years but the technical part of is not a big job.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Thank you, Dr Deere.  Just finally on the water safety plan, this control process content, can that be an appendix or a section which can be added in a sort of modular way and updated?

- Yes.  I –

- Kept fresh?

- Yeah, I agree with the Panels earlier position that that would be the sort of thing that might be in the executive summary and we’d normally design it as a pullout that will be – we sort of talked about it as being all the operator needs to know.  We've got this great big water safety plan required by the regulator, required by the managers, required by your expert reviewers.  What the operators need to know, they need that core day-to-day information about how they're managing water safety.  If you follow what's in this, maybe a few pages, if you follow that and do that, we know the water is safe.  The water safety plan explains why but, you know, that’s interesting but what you need to ensure is you meet that and we often see those pullout sections literally plastered on the walls in the depots, in the treatment plants, in little small little ring binders, often they're laminated and that becomes their control document.  If you update one, you’ve got to find them all and put the new ones in and in modern systems, they're often built into the process control electronics card systems and you can open a page, press the water safety plan button and it shows those critical processes and shows those controls.  So there needs to be a pullout.  Whether it's appended up front doesn’t really matter as long as you can pull it out and give to people who need to know.  There may be different ones too for the operator who manages a network may have a different part from at the treatment plant depending how you structure the organisation.  It wouldn't always be a single pullout.  It could be multiple pullouts.

MR WILSON:

- But the point you make is that because of its importance, it needs to be a control document in a top quality management system?

- Correct.  As with any other quality management system, it becomes a quality critical document, probably the most important document you’ve got.  It sets out what you have to achieve day-to-day.  So if that changes, you’ve got to withdraw the old versions and replace with the new versions, as with any quality control document, any quality system.  It's no different from manufacturing a car or, you know, as I say, a McDonald’s hamburger.  The, exactly the same concept applies.

- Well, that leads us to a logical question, which would be, how mature is Hastings District Council’s quality management system?

- I don’t know the answer to that.  I’ve not looked at how they manage documents.  Fortunately, the Water Safety Plan, there aren’t that many of those documents, so it may be they could develop, if they haven't got one all right, quality control systems just for those quality critical documents.  I don’t know if they got a full ISO 9000 or one type quality system gen – as a Council, I don’t know, I’ve not looked at that.  That's a good question though.

JUSTICE STEVENS:

- I’d like to explore briefly the political aspect of implementation of this type of document, because that would be highly – it will become really important to us in August, the August hearing and help us in terms of our recommendations.  But the short point is that in your dealings with the District Council, you have had no pushback at all in terms of your suggestion that the Water Safety Plan be upgraded to meet best practice?

- No.  It's not – for them, it's not a big change, it's just a case of documenting things that they already do and they are more than happy to do it.  The reason they hadn’t done it and they explained to me was because the Regulation didn't require it and their Water Safety Plan has to be approved and meet the Regulation.

- But the short point is in response to any potential downstream political pushback is for HDC it's not a big cost?

- No it shouldn't be – I don’t see a big cost, no.  And they’ve asked, in fact, they’ve asked me to help them draft those components.

- Yes.

- There’s been no pushback, no.  And often one of the points that was made was that most of the things I was saying have to be documented and formalised are already somewhat documented and formalised –

- Yes.

- - in Council, they just haven't been brought together into that nice coherent summary to allow a Drinking Water Assessor or another party in Council to see that it's there in one place.

- Which suggests that given at least that example, any suggested pushback in terms of cost needs to be carefully examined?

- It does.  Where the costs may come in, for example, is if the operator hasn’t got enough time to do the checks you might require or if the checks find problems.  And one of the most common – for example, it's not directly relevant to this particular incident, but in mature Water Safety Plan jurisdiction that have had longstanding Water Safety Plans, the treatment normally gets well and truly controlled and gets sorted out. The most common failure we are seeing now in Water Safety Plans and there was a recent presentation by the Victorian Health Department on this to its Water Utilities in Australia, we’ve seen it in other countries as well, in the US CDC have made this point in it because they’re global – they’re National Centre For Disease Control, is what we are now seeing is lots of problems with reservoir storages, where they get birds in the reservoir and pathogens get in, campylobacter and things through those.  That then requires operators to go out there in certain frequency to fix the roofs and do things and they haven't – often there is not enough staff in the Council to do that.  That is where we may get pushback is when they write the Water Safety Plan, they realise we should be doing that once a week, we’re doing it once a year, how are we gonna manage that?  That’s where there can be pushback.  But what we can do there is we can say to the Council, “Write down they do it once a year and have an improvement action plan to try to improve that resourcing in the longer term, so the current plan reflects current practice, we acknowledge the gap and we have an improvement action.”  And the current Water Safety Plan that Council has does have an improvement action plan as part of it and the current Water Safety Plan model that the New Zealand Regulations have does cover improvement plans.  So you have got a place to put it and then you can systematically manage it.

MR WILSON:

- But that raises an interesting question, I mean, in the Scottish system there used to be a concept called “undertakings” where –

- Yes.

- – where one undertook to do certain things in certain times.  The problem was, what was the censure in the event that the undertaking wasn’t followed through?  In that particular case, it was restructuring the industry, but the question is, what happens if an improvement plan is not followed through on, does the – do the deficiencies just get carried through into the new version of the Water Safety Plan or does the Water Safety Plan become non-compliant?

- Well that, yeah, the same term is used in Water Safety Plans in Australia as well and in other jurisdictions, a term “undertaking.”  It's taken very seriously because those undertakings get audited and if there is a failure then they will in the annual report, you know, it will be published that they failed to comply.  So far, or from what I have seen, the public humiliation of having a failed Water Safety Plan has been enough of a threat to avoid Councils or other parties just ignoring that, but if that were ignored, I don’t know what you’d do.  I mean, I’ve not seen – the Public Health Department if they’re prepared to stand up and say, “This isn't good enough,” they community won’t accept that as a rule and the Council will fix it.  But that won’t happen politically if that was too hard to say.

- Well this is a discussion for August but the Ministry of Health here have been reporting for 10 years that 20 percent of the population are not being supplied with water that meets the Drinking Water Standards and yet that public opprobrium doesn’t appear to be sufficient to encourage those water suppliers to sort their act out.

- Yes sounds like – your example from Scotland where they sort of put the threat of restructure of the industry, is the sort of thing that might have to be put out there.  Say if you can’t get your act together – because you can make any industry structure work, we can say this industry structure we have got now is working, we will keep it.  But you can say if it doesn’t work, then we will have to look at other structures.  But I don’t have a scientific answer to that, that is a political structure but so far from what I have seen, if the Health Department is prepared to stick its neck out and where the political flack of creating a possible cost impasse by saying this isn’t good enough, if the Health Department can be the bad cop, then the Council can then begrudgingly say to the public, oh well back luck, we have to increase the water price and fix it and they have been prepared to do that.  But as long as they can blame the Health Department, they are usually happy to do it.  Similarly with fluoride, they don’t like adding fluoride to water, but they  will do it if the Health Department tells them to.  And they will just tell the ratepayers, bad luck we have to do it. But someone has to have the political support to do that and that can be difficult.

JUSTICE STEVENS ADDRESSES MS ARAPERE:

I just want to ask Ms Arapere a question.  Are you or Ms Butler dealing with the Ministry of Health side of things.

MS ARAPERE:

We are Sir.

JUSTICE STEVENS:

Having heard about these current best practice, are you going to be providing relevant material in the Ministry of Health submission for August that deals with all of this?

MS ARAPERE:

That is our intention Sir and in fact while we have been sitting in the hearing, we have been trying to seek instructions so that we can give you an earlier answer than the 21st of July.

JUSTICE STEVENS:

Because what I would be very interested to know is whether we are going to get any push back on what seems blindingly sensible, that you know, in a sense it is a pity that New Zealand has fallen behind.  That there is a very good model, according to Dr Deere and we have had independent information from Dr Fricker confirming this.  It does seem or I imagine that our Ministry of Health would want to see that New Zealand standards brought up to best practice.  So if we are going to reach a consensus around that, then the early advice would be appreciated because it is going  to impact on the work of counsel assisting.  It is going to impact on responses by other parties and it is going to impact on how much further we need to hear from Dr Deere and others.

MS ARAPERE:

So thank you Sir and in fact Ms Butler was on the telephone to the Minister of Health during the break and as quickly as we can, we will be able to update the Inquiry on that.

JUSTICE STEVENS:

That would be very much appreciated and thank you very much indeed.  I think you will have gauged the fact that Dr Deere is talking to an open door.

MS ARAPERE:

We have certainly gauged that Sir.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Dr Deere can we now look at the question of the Emeergency Response Plan.  Have you advised HDC on this?

- Yes and my advice was that the Emeergency Response Plan isn’t in a form that I would want to pull out in an emergency.  It needs to have some clearer summary information that can be used in an emergency if a key person is not available and so Council has agreed to – well they have asked me to do that, to get those little sort of key extracts so I have given examples of the sort of things I am used to seeing.  Things like very simple one page, fit to a page tables, or diagrams show, if this, this is what you do here to your contact.  And the Ministry of Health guidance has some examples like that in it as well, so it supports that approach. So I'm suggesting that that is those little summaries are prepared that are in a form that can sit in an incident room and sit in the chief executive’s office or other parties offices and they can pull it out if they need it and find where they will need to be straightaway and use it.  So often these documents have little tabs that you can find things quickly.

- A quick reference manual?

- Yes, they have to work in, you know, you have to fundamentally work in an emergency.  It has to be technically accurate and explain why it's the way it is but it has to also work in an emergency.

- In your view, should New Zealand have either a prescription or a guidance for the content for an ERP?

- That’s a good question.  They probably find its most organisations, they put their drinking water quality Emeergency Response Plan, they link it to their other Emeergency Response Plans.  So they have an emergency planning process that deals with all kinds of emergencies and so they tend to be better captured in that format and there is guidance on emergency response, generic guidance on emergency response preparedness and planning that Councils have for all kinds of emergencies.  So if we were to provide guidance on a drinking water quality Emeergency Response Plan, the danger is you’ve got this clash between that and the other emergencies and incidents that Councils manage.  So their preference usually is to try to put the water quality part into their generic incident response plan with that generic incident response framework.  So as a water quality person, it'd be nice to have my blinkers on and do it the way we like it to be done, but I acknowledge that that’s not how incident management usually works.

- In this case, the ERP is now an appendix to the WSP isn't it?

- Correct.

JUSTICE STEVENS:

- And you are comfortable with that obviously?

- It's easier for me with my water blinkers on to see it in isolation but I acknowledge that if we had a guideline that says you must do an ERP this way, many Councils will say that doesn’t fit with our emergency response frameworks and there are other guidelines as a whole sort of, a whole separate professional world of expertise in emergency preparedness and planning and so that would get some, I think, some legitimate push back from Councils that would rather build it into those frameworks but what it could be and the reason the guidelines is some, a few key principles such as making sure it's clear, that you have the contact names and numbers, backup contacts names and numbers and the key point the Panels’ been making about absolute clarity of who makes decisions and when can it get elevated and there needs to be at the very least some, and the New Zealand Guidelines provide examples of those, some key pullout process decision support flow diagrams that explain how to respond to things.  If you get an E. coli result in the water, where do you go next?  What's the next step you take?  How do you follow it up?  That needs to be predefined but that can be described as the guidelines currently do in generic form.  I don’t know that it's, that that’s lacking at this stage.

- I do not see the two as being mutually exclusive in the sense that you could have guidelines for your emergency response for campylobacter in the water or such an event and once those requirements are met, if it delivers a part of the water safety plan or indeed is part of your emergency response says, in two places.  I mean it is better than having them nowhere.

- Correct.  I agree with that.

- So I take your point but let us not see it as a barrier, rather an opportunity.

- I mean certainly if the Guidelines, certainly guidelines are helpful provided Councils have the opportunity to depart from those if they have better ways they like to, you know, the complaint we get when we have guidelines, people say well, I've got a better way but they feel obliged to follow the guidelines.  If the guidelines are there as examples, which is what the current framework is set up to have, the current Ministry of Health framework has examples and templates, providing templates would be, you know, helpful in that context as long as Councils are able to use better options if they’ve got them.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- In your experience or in your view, how frequently should an ERP be updated?

- ERPs I think are usually seen as living documents simply because the core information that, about the contact, peoples’ contact numbers, contact details and the trigger levels for action change quite frequently.  So they have to be living documents.  They might have a full update at least annually, a full review and update.  Not much might change at that frequency.  There should be a formalised capture, we've reviewed it, we may or may not have changed it but it's also got to be seen as a living document as well and that creates problems where those documents need to be submitted to regulators because it can't change a person’s name and then submit the document.  So the, what the regulators often do is talk about if substantive changes are made, send us new version, if you make minor changes in the interim, just keep that version 1.3, version 1.4, only send us version 2.  But there should be, you know, and I think Craig made the same point earlier that, Mr Thew made the same point earlier, that probably annually there would be a stand back review, it may or may not change, I’d agree with that sort of frequency.  That’s what I am used to seeing.  That’s part of the annual process.

MR WILSON:

- But with living documents, it is not essential to embed some of the information in a document, but you are capable to link it to other data sets.  By way of example, it would be important to have a list of food and beverage outlets in a Water Safety Plan?

- Correct, absolutely, hospitals and all those sorts of – yes, correct.

- The vulnerable, but just take the food and safety outlets.  Local authorities in New Zealand are also the food and safety regulator and therefore they have a data base of all of those outlets in their environmental health register.  There is no need to duplicate that data set in written form in the Water Safety Plan as long as you have got a robust link to it so that you can, in emergency, action – act – access it and be able to advise that.  In that way, that part of the plan became – is automatically updated as they – as that data set changes.  I mean, do you support that approach?

- Absolutely, yeah.  In principle, it is best not to replicate things if you can find them.  The only caution I would urge there is that people often put hyperlinks, like electronic links, then of course one of the most common cause incidents is power failure which affects water and everything else and they can't get the hyperlink.  So if is a hard – there needs to be some reference to where the hard copies are as well as just a hyperlink, it can't just be a hyperlink.  That’s – people have fallen over using hyperlinks to things because of power failure is a common failure in modum water supply.  But other than that, I agree totally with that.

CROSS-EXAM INATION CONTINUES:  Mr Gedye

- Can you throw any light on the one minute in the pan and immediate boiling in the electric jug issue?

- Yeah, so that’s come about because and as a scientist that seemed ridiculous to me why would you boil for a minute, as you said, in fact 60 degrees in a hot water system is usually enough to kill all the pathogens we are concerned about.  The problem though is that what was explained to me by the public health professionals is that if you say “Just boil in a pan,” people see bubbles at the bottom of the pan, which are forming at the bottom and think that means it is boiling, so they talk about “getting it to a rolling boil,” which means there is enough turn-over in the water that is physically moving and they – some of them say a minute, some say five minutes, some say two minutes, there are different guidelines.  It's based on the fact that your definition of boiling and my definition of boiling might be different.  So it's an awkward area, it's an awkward area.  With the electric kettles, even ones that aren’t very accurate, normally turn off above 90 degrees Celsius, they normally – usually close to 100.  And so they are very reliable in that sense, but boiling in a pan is relying on the person to know when it is boiling and bubbles at the bottom of a pan is not boiling and that is the problem.

DR POUTASI:

- Can I just check, you don’t disagree though with the WHO definition of “rolling boil”?

- No, I think it's – pragmatically, that’s about the best you can do.

- Yes.

- If it was me, if I was at home doing it, I feel I’d be confident to know when it was hot enough and I wouldn't be letting it go to a rolling boil, but how do you provide that advice to a general – in a general sense?  The rolling boil is a good measure of a really solid boil.  It would be pasteurised and safe well before that, but when do you – where do you draw the line?  So that's the problem and as the point was made by Mr Thew earlier, we often do have power cuts and we have water problems and so people are forced to use gas or other methods of heating.

MR WILSON:

- So if one was to give a single piece of advice, the single piece of advice would be “a rolling boil,” because an electric jug of itself is - do – automatic ones do switch off above a rolling boil anyway?

- Correct.  There has been confusion in the past where we said – just issued the instruction for rolling boil.  People have held their kettle buttons down and caused problems.  And so as a result of that, the advice is now, “If you have got an electric kettle, just use the electric kettle.  If you haven't got the electric kettle, then use the rolling boil.”  We try and deliberately separate those two because of the problem of electric – we had, I mean, the Sydney water incident was a good example.  The costs and implications of the boil orders that were issued were huge.  People causing electrical problems with their kettles.  There was some work done and that Dr Fricker was aware of by Thames Water in London looking at the number scalds that arose during boil orders, people are getting scalded by having their kettles spilling over and things like that.  There was a serious health implications.  So it's a very imperfect way of solving the problem, but the best advice we’ve got is this sort of one or sometimes other departments use more than one minute, but this rolling boil concept for pans and electric kettle just wait until it turns itself off automatically.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Looking at the Hawkes Bay District Health Board fact sheet, have you yourself ever bathed in bottled water, Dr Deere?

- No, I haven't but I've often, I mean I've done a lot of work in developing countries and places that have unsafe water and I've often used bottled water for, you know, brushing teeth and so on and the bathing in that context would have just been if you want, your wiping the baby down with a cloth or something like that, yeah, it wouldn't be, you certainly wouldn't have a bath in it, no.  I think the term bathe in that context is intended to refer to if you’ve got, you know, ,trying to tend to a wound or wipe down a baby after the nappy change, that sort of thing rather than a bath.  I think it's just the use of the term.  It's the many parts of the world where that’s, the tap water is never safe and people do have to use bottled water for a lot of personal hygiene activities that you might term bathing but not having a bath, no.

- So the current ERP could be improved by having a quick reference manual or an extract which is a short usable document?

- What I'm used to seeing is a hardcopy, in a hardcopy version, is very clear tabs so you know where to turn and very clear simple diagrams designed to fit to a page that show the actions you take and the table of contents will say, “This tab if you’ve got an E. coli, this tab if a chlorination fails and this tab if you,” and then it'll, for example, you mentioned if you're going to talk to the food industry, you need to know when the water is not safe or the hospitals, where to find that information.  So well indexed, well referenced and designed as a user-friendly document.  So what we have at the moment is a document that can be easily turned into that form but at the moment it's more of a version for the Ministry of Health to look at that summarises the process rather than the user-friendly operator version.

JUSTICE STEVENS:

- And just in terms of your work for the District Council, you are getting no pushback on that at all?

- No, no.  No problems.  The Council’s been very open and transparent and with all those, all those sorts of matters.

- Good.  So we have to just make sure that if we were minded to accept your evidence and recommendation, in a sense to adopt world best practice, that we thought through any implications of implementation.

- Yeah, the only – 'cos the Council hasn’t been pushing back on things.  The concern I had which is sort of, was a sort of my sympathy for Council staff and Council as an organisation, was that I thought there were some things that I saw of his, and I think Ms Casey made the point, describing them as, I think she used the term, important but not urgent.  There were things that I would want Council to be able to park so they can focus on the more important priorities or the more urgent priorities and that’s the only worry I had.  The Council hasn’t been pushing back on things but I've said to them I think you’ve got to be careful not to get overwhelmed and not so much push back but just put into a later, not saying they're not going to do them but put them into a longer term programme.

- I think that is a very helpful observation and it is probably, speaking for myself, something that we would identify with and share because the District Council has been through a very difficult period and that is why we raised with you earlier the relative importance of developing a strategy and making sure that the truly urgent decisions are made in a timely fashion.

- Yes.

- So we take on board that portion.

- And it would make sense then to reflect that back to you so you can see that Council’s been given your advice and they’ve said these things we were going to do in five years, these in two years, they’ve not ignored it or pushed it back and provide that back to you to show that.  Yes, it makes sense.

- And indeed August, we have further hearings in early August.  So that may well – or they can talk to counsel assisting at any time.

- Yes.

- I mean our doors are open and it is inquisitorial, so it is a very good process and for example, the point arising from Ms Casey’s questions.  You can pick up the phone and talk to Dr Fricker at any time.

- Yes.

- And in that context, the exchange of views of experts is important.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Do you have a copy of the ERP there in the boxes Dr Deere?

- Yes.

- If you look at page 25, should be in tab 6 for the panel.

- I have got the WSP here.

- Do you have the ERP as well?

JUSTICE STEVENS:

- It is in tab 6 but Mr Thew is going to provide you with a copy.

- Thank you very much.

CROSS-EXAMINATION CONTINUES:  mr gedye

- It is a table of 4.3..9.1

- It is the same one, yes.

- I just wanted to ask you about the adequacy of the response protocols and to suggest that the current table is pretty simple and effectively just provides for re-sampling but that you could improve this considerably by looking at investigating things like total Coliforms, turbidity, loss of residual, ammonia, pressure and things like that.  Is that part of what is comprehended in that yellow improvement item?

- Correct.  So Council started work on a programme to collate data so that it is all available rapidly.  So if they get an adverse result, they can interpret it with the knowledge of the other results and that is very important and can avoid the crying wolf programme that then leads to complacency when you get a real problem and it also means that you can interpret results in the context and make a decision about how widespread an incident might be, which areas it affects, and what the right action might be, so that is exactly right, that is what the Council is working on now.

- And in fact there is a number of improvements items through the document aren’t there?

- Yes.

JUSTICE STEVENS:

- Those are the ones highlighted in yellow?

- Yes.

CROSS-EXAMINATION CONTINUES:  mr gedye

- I am not sure and I will ask Mr Wood what interest the DWA has in this document but it is not a formally regulated document is it so you could change this as frequently as you wanted to and just have continual updates until it is in the form you want.  Is that your understanding?

- I am not sure because if it is submitted as part of the Water Safety Plan that is approved, I am not sure to what extent that is seen then as – I am not sure, so I don’t have the answer.

- In fact it is a different animal isn’t it really from a Water Safety Plan, an ERP and it can stand separately can’t it?

- Correct.  The Water Safety Plan normally tells you when you go to the ERP and then the ERP then deals with the responses to those incidents.

- This quick reference manual you have talked about.  Would that be lodged with the DHB and the HBRW and other agencies who may have an interest in systems you are familiar with?

- The parts that they need to be involved with are normally shared in terms of getting agreement.  This one will contact DHB, DHB might agree to that.  They may not keep a copy of it themselves, just because of the issue of version control however but you want to be absolutely certain that when you said you are going to contact the Regional Council or the DHB, that they understood and agreed that that was the case where is where the Joint Working Group type concept is quite useful to review those plans.  But normally because of version control, I wouldn’t expect them to have a full copy of every Council’s response plan.

- I am moving off the ERP is the Panel wants to ask any more questions.

QUESTIONS FROM THE PANEL – NIL (IN RELATION TO ERP)

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- I want to ask you about laboratories and testing and sampling.  Only fairly briefly, based on what you have seen, have you any concerns about the level of competence and service provided by samplers and laboratories in this region?

- It is clear and I think you have had this discussed earlier, in earlier hearings, that the local capacity was overwhelmed for a time and that some mistakes were made.  So the example that I was surprised to see was that the samplers were collecting chlorinated water but they hadn’t added the standard thiosulphate neutralising agent which is you know, worldwide, it has been going on for decades, as a bog-standard practice.  I was surprised they were doing that.  That suggested a lack of experience and expertise, even in the most basic area; however there has been a lot of scrutiny and advice and the labs been moving up to get up to speed.  I haven't done an assessment – a proper – I am a laboratory assessor, so I can do assessments of laboratories, I haven't done a proper laboratory assessment as such, but the more recent results look much more consistent with what would be expected and the – I interviewed briefly the Protozoa lab in Palmerston, Massey University, and I interviewed briefly the local routine microbiology lab and they seem to be aware of those problems and across the need to fix them.  What they didn't have which surprised me a bit was that if you look at this courthouse, for example, you’ve got your – it's a custom-built courthouse, you’ve got all the right things you’d expect in a courthouse.  If we could do this Court hearing in the local canteen, but it would be a bit awkward.  The local laboratory didn't have a custom-built lab and I’m used to working in custom – you know, custom-built labs, they have all the appropriate water systems, air flow systems, cabinets, it literally was a warehouse that had been converted into a lab.  So their job is challenging, doesn’t mean it can't be done well, but it wasn’t a custom-built microbiology lab that I am used to seeing.

JUSTICE STEVENS:

- Did understand Mr Thew’s answer this morning that you have still got a couple of further interviews to have?

- Correct.

- So that’s – so the one at Palmerston, was that the one attached to Massey?

- Correct and that’s a fully set up laboratory that has all the equipment and so-forth.  The local lab that we looked at that was quite a new lab, they seem to be full across the issues, they explained what they were doing and about things that had gone wrong in the past and fixes.  We didn't do a full audit and so while I’m here, one of my actions is to go and visit them again and look for – look at how they are progressing, but what I noticed with the local lab, they weren't, as Massey University is, a custom-built laboratory.  They were a local industrial sort of business area that they’d got a unit and been turned it into a lab and it was – I didn't go past the front – I only stayed at the reception area and interviewed the people at reception area, I didn't go into the lab and do a laboratory audit, so I couldn't really advise if the lab is up to standard or not, but that – my observation was it wasn’t a high-capacity commercially or, you know, Government hospital sort of type custom laboratory, it was a small local business operating in a warehouse, as it were, so –

- Because this may have implications for accreditation?

- It may have.  It's, as I said, you know, I said we could do the Court hearing in a school canteen sort of thing, as an example, you could still meet the accreditation requirements in that environment, but it would obviously be more challenging and I didn't walk away feeling that sense of, “Oh, this place has been running for 30 years, they’ve had 50 audits, they’ve got,” you know, it didn't have that sense you get in most commercial labs they are extremely well set up, they have pharmaceutical clients, food clients, they are being audited all the time, it wasn’t that – I didn’t get that sense.  But it may be that there work is now perfectly adequate, but I can't give that, you know, I can't give that view.  What I can say is it is not a conventional commercial or a Government water lab that I am used to looking at.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- In your experience, would it be true to say that the bigger the water supplier, the better access it has to laboratory facilities just because of the resources that scale brings?

- Yes, so most water laboratories have numerous clients, or they are the lab that is owned by a big water utility.  So if they are private labs, they might have hundreds of water clients from pharmaceuticals, food, drinking water, or it's a water utilities own lab or a health – it can be a health department or hospital lab.  So you are absolutely right, you wouldn't, you wouldn't expect a small Council to have its own water lab.  If they did, it might just do a few routine tests, simple tests such as like chlorine and so-on and minor tests, but the – once you get to the more complex microbiology and chemistry, that normally goes to a lab that services multiple Councils.

- If you got an anomalous result back from a lab and I give you an example, one FAC reading we have seen is at 46 milligrams per litre.

- Mhm.

- What would you do about that, in terms of the laboratory?

- I would normally want a full root-cause analysis.  So how did that – where was the mistake made?  Was it a typographical error? Was it a real reading, if so, how is that possible?  Was it a typographical error, was it a data entry error, was it a measurement – a full root cause analysis and explanation and labs normally have that sort of procedure as part of their standard process to follow that up.

- If an E.coli test was done with a presence reading and then the lab raised the possibility that it was caused by cross-contamination within the lab, what would you do about that, as the water supplier?

- That’s probably the most common reason I get asked to go and investigate labs is when people think they’ve got a false positive and then we go through the whole process from where the sample container has come from, how they're handled, how they're pre-treated with thiosulphate addition, how they get carried out by the sampler, how they come back, where they go.  If I found for example, that I have found in some cases, the sewage sample has come back from the sewerage plant covered in dirt, sitting on the same bench as the water samples coming back from the water samples, you can say cross-contamination can very easily arise on a little bit of dust between the two.  I'd want them to explain how they control cross-contamination in full detail and witness how that was done.  The difficulty with, in a situation we've got in with the current lab is the sheer volume of material they're handling would make it difficult to carry out an investigation, so one of the recommendations that I think Dr Fricker also had was if they can slow down a bit on some of the baseline sampling, move to more event-based sampling, it allows more time to follow up those sort of things in-depth and detail but when they're overwhelmed, there's a higher risk of cross-contamination and it's much more difficult to follow it up but there should be a full follow up 'cos that’s one of the most common causes of E. coli detection is, in a good water supply system, is false positives arising from these sorts of events.  It's very very hard to prove it so you want to try to eliminate as many of those as possible.

- Have you been able to form any impression on the adequacy of the samplers and the sampling process?

- There was a concern Council had and I had as well and Council’s taken steps to ensure the samplers are part of the laboratory and properly trained and so on.  It's an area I think of probably, I'll call it paranoia by many water utilities because they’ve seen so many examples of what they believe are sample errors.  So what we try set up these days is a dedicated sample taps that can be flushed and can be flamed to ensure there's no risk of contamination on the tap.  Often there's a cover to stop things like bird droppings or dust falling out of the sky or no overhanging trees.  The samplers then have to be properly trained and have competency assessment, a weakness competency assessment.  Only the samplers can take the samples.  They keep records.  They must show utilities like a barcode scanner or some other evidence that they were at that sample tap at that time to prove that samples from that location, the sample tap should be clearly labeled to ensure we know that we’ve got the right sample and some of the processes aren’t yet up to speed.

- Do you know what’s being done about getting them up to speed in Hawkes Bay?

- So far the discussion I had with Mr Thew that they’ve looked to ensure that the samplers are from the lab, that they are trained in that area.  I’ve not followed that up on this visit there to find out what’s happened but that’s the only way that the Council and is working on.

- Would I be right to say that all of these laboratory and sampling issues are crucial links in the safety chain both from the point of view of potentially missing a pathogen but also creating a reliable database that can be relied on?

- Correct.  And unfortunately even in the most advanced utilities, there are still holes, there are still situations where you get, as we’ve seen in your examples, where you get data that just don’t look right and nobody can explain and I won’t name names but I’ve been dealing with, I often get given spreadsheets and data from even for the best utilities, top utilities, and there’s some results that just don’t look right and sometimes nobody can explain how they got there.  So it’s area that requires ongoing vigilance and I’ve seen water utilities spend millions of dollars on monitoring programmes and throw the entire dataset away because the controls and processes weren’t right and it’s one of the comments I made in my observations when I first visited Council was they haven’t had much engagement with microbiologists and although it hasn’t happened to them, I’ve seen institutions that have spent millions on testing and had to throw it all away because they haven’t engaged with people who understood the testing.  So it’s an area that’s, that Council could improve but you can say that about just about everybody’s monitoring programme.

- Well, that would imply a need for a substantial level of vigilance and accreditation and auditing, correct?

- Absolutely, and also in the fourth category is proficiency which is where the lab should be taking part in blind or double-blinded or single-blinded proficiency trials as well as the auditing and accreditation training.  So in other words, they get samples and they report on them and they have no idea what’s in that sample but someone does and so that should be part of it as well and that is what I am used to seeing as part of these controls and they have hospital labs, diagnostic labs, pharmaceutical labs, food safety labs, you get the same principles apply there.  There is nothing different about water. Water isn’t sometimes quite as well managed as some of those labs because most of the samples don’t show anything of concern, but the same principles apply.

JUSTICE STEVENS:

- Can you just shed some light for us on – you are describing what you are familiar with in terms of best practice.  Do standards emanate from what source?  Are they statutory or are they again World Health Organisation or models or what?

- There is a term like good laboratory practice that is used and there are various models so the IANZ system, for example, in New Zealand sets the guidance.  So if you are accredited for measuring E.coli in water there is guidance by what that involves.  A lot of it though is unwritten so some of it is just experience practice so there is a lot of peer review involved in that process, so the laboratory assess and then we make some judgment about things.  Some of the things that you might think are obvious, aren’t written because they are seen as too obvious and they are missing from those sorts of guidance manuals.  But in general the GLP, the Good Laboratory Practice guidance that is used in the IANZ protocols are considered adequate.  But I don’t think – I think the issue is just getting the lab up to speed with that and giving them the time they need to get up to speed rather than a lack of protocols and procedures to draw from.

- And not being overwhelmed with volume so that the risks are increased?

- Correct.  And to me it is prioritising what they do to make sure they can do it well.  It is always better to have less good data than lots of misleading, confusing data.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Have you looked at IANZ accreditation curriculum and levels?

- No I haven’t.  I am only involved in the Australian equivalent, the NATA system, I am an assessor under their system.  I haven’t looked t the IANZ system in detail.  I would be surprised if there is anything fundamentally wrong with it although Mr Thew advised me today that he noted that he thinks the samplers, there is no system for accrediting samplers for example and I think that would be a gap.

- Yes we are looking at samplers, it is a weakness.

- Yes.

- Much of what you say would indicate that, to get a highly competent well resourced laboratory, it is going to need to be of quite big scale, have quite big business.  Is it workable to have a laboratory only in the main cities or does it need to be geographically close.  Does HDC need a laboratory in Hawke’s Bay?

- In general, even the big laboratory organisations, still have lots of small laboratories because the transport of samples, the physical transport of samples causes a major problem for turnaround and preservation.  So those local tests like the E.coli for example, the common local tests, a city this size would normally have a lab that could do that.  It may be owned by or linked to or collaborating with a bigger lab and that’s common to help it with its good laboratory practices and so on in training and competencies and back up staff and so on.  But the actual physical testing of things like E.coli and IM and the common tests that are done in water, would normally be done locally.

- Can a client, like HDC, achieve high standards contractually.  In other words it says, well IANZ may or may not be adequate but we are going to set our own levels and our own auditing systems by contract.  Have you seen that?

- That’s normal.  IANZ or NATA, the Australian equivalent, we have set up these, what we call the lowest common denominator which is not always as good as what you would like to see and so most water authorities and Councils have some extra requirements they would like to see beyond that and in many cases they will even have their own separate – say for example, for error samples, only this bench can be used to receive those bottles, they mustn’t get mixed with other peoples’ samples.  Only this equipment can be used and so on so they often have quite special requirements to really ensure and that is quite common practice, there is no reason the lab can’t agree to that.

MR WILSON:

But having said that, the organisations that are requiring those, are large competent specialist water.

They are and they normally employ people who have a laboratory background.  They may not now be in the lab, they have probably come through the lab system at some point in their career, they know what questions to ask.  They are a smart client, so they know what they are buying.  Where they have been getting into problems is where they haven’t had a smart client and they have been getting into problems is where they haven't had a smart client and they’ve been getting, as I say, sometimes millions of dollars of test results they just couldn't use.  The lab was following what the Guidelines said, the local IANZ or equivalent standards, it did everything right, but the data was useless because of that lack of appreciation of the subtleties that sometimes come into play.

- But it's implicit that there is a certain critical mass to be able to afford a smart buyer?

- Yeah, that’s right.  You know, you’ve either got to have enough capacity to have that in-house expertise or enough capacity to source an expert to help you write those terms of reference and write those briefs.  Or it could be a peer review-based process.  It may be that you have a neighbouring Council that has got an ex-lab microbiologist that can help you and you’ve got an ex-lab chemist and you can sort of collaborate.  It can be done by these – I’ve often seen these things, they call them – in Australia we use the Regional Organisation of Councils set-up and they’ll decide who their regional expert is for that area and they’ll help write terms of reference and do audits and checks on the labs or other specialist areas.  So there is ways and means of achieving that, but you’ve certainly got to have enough capacity to know what questions to ask or who to ask the questions of.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- If necessary, you could help Hastings District Council with that?

- Correct.  That’s – and that’s one area that Dr Fricker when I met him in Auckland he was saying he was frustrated, he wanted to help them, but he felt he couldn't do that, but he could see how he could help them, so he said that I should be doing some of that assistance, correct.  So writing the terms of reference, the contract specifications, and also looking at what the auditing and proficiency requirements are for the lab and need to be down at the level of specific tests and specific staff, it can't just be – can't be too generic, it's got to be quite specific.

- So if HDC has any concerns at all, perhaps about samplers, you could  write a contract specification that nailed that down to the precise robust requirements that were safe?

- Correct and it would probably also include at some recognition of accredited samplers and also the competency assessment processes given that status.  And the only other caution I put on there is that we have found we have had problems with incidents where samplers have been and in one case literally going to the local pie shop and taking samples and handing them in and literally was that case and that was an incident that was an outbreak actually that was missed because of that.   So I would recommend these as I recommend – it's very easy to do with modern smart phones and things – I recommend GPS time stamping when the samples are taken as well as a final check that Council should have so it knows it's samples were taken at that point at that time because there have been problems in the past with competent samplers not doing what they are supposed to be doing.

- I didn't quite follow what you meant.  Do you mean the sampler didn't go to the right sampling tap, it went to the pie shop instead?

- Correct.  They went to the pie shop and just filed the bottles, had a pie, came back and they missed the samples from the bore that was contaminated.  So that has happened and that's just – and so now, good practice now would involve  and it's easy, very easy to do, as I say, it's just, you know, a smart phone app that can do it and it's freely available is, you know, it's not difficult, but you time and date stamp and location stamp when you get the sample, so that you know the person got to that site.  That would be unusual for a sampler to do that, most of them are very conscientious, but if I was a Council and I was contracting that out, I would think, “They’re not my staff, I can't control them, I’d want to have some certainty they went to that location at that time and date, I want that record.”  It's easy to do, so –

JUSTICE STEVENS:

- Just a further development of this same theme, we are obviously going to be looking at this again in August and so any updates that can be provided will be valuable.  There will also be, as I understand it, a fact paper that the Ministry of Health will provide on laboratories, the IANZ accreditations and other aspects of sampling and testing.  So it may be helpful if you can have a look at that when it is – comes out.

- Yeah, there also needs to be a communication version of that, too.  Because if they write that for the microbiologist and the chemists in the lab, the danger with some of the Councils won't realise that there can be flaws with that.  So a good example is the lab is IANZ accredited for, say, E.coli, but not for, say, mercury, but he Council thinks, “That’s an IANZ accredited lab, you can test mercury.”  The IANZ system deals with specific tests in specific matrices, so maybe it's tested – they can do E.coli in food but not water and specific contexts.  So the Councils need to have the guidance health producers for the laboratories, there need to be some kind of plan language version for the Councils that says, “Your contracts should make sure you’re testing for the right things in the right water or the right water types with the right people with the right methods.”  It needs to be a user-friendly version I think as well, because I find that I’m often translating that and that’s inefficient, that could be in a simple guidance document just done once and then it's done.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- I’d like to turn to Protozoa and the risk from Protozoa.

JUSTICE STEVENS:

Just pause there.  Dr Poutasi did you have any further questions?

DR POUTASI:

No.

MR WILSON:

No, I’m fine thanks.

JUSTICE STEVENS:

Thank you, Mr Gedye.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Do you accept or am I right that there is a correlation between wet weather and cryptosporidium?

- Correct, so there was – it was an analysis done by the CDC on I think there was a 300-odd outbreak so I can't give you that figure, a lot of outbreaks of water-borne disease in the US from their database and over half followed what they considered to be increased wet weather events and the same is true for cryptosporidium outbreaks as well and that's most water-borne disease outbreaks that arise from a source, the arise when fresh pathogens flow which is after a rain event.

- Sydney had torrential rain before 1998, didn't it?

- Correct.

- So would you generally favour a high level of attention to wet weather events, generally?

- Correct.  And in fact there is a recent study from Canada was published so just a few weeks ago where they took – they did hourly samples for pathogens to show just how rapid those rises and falls are and in wet weather the concentrations can increase thousands of times and drop back down again very quickly.  It's the extreme variability that we get in wet weather of pathogens.  So almost all the risk from source-related contamination typically arises in wet weather and so if you are going to prioritise your monitoring and management it makes sense to focus on wet weather events.

JUSTICE STEVENS:

- Do you want to just give us a primer on what it is of the wet weather that causes the problems?

- Yes, the hydraulic flow across the land surface that drives faecal matter off the surface into water and with ground water it then can short-circuit through at surface – higher levels and find its way into cracks and fissures and then into the bores as well, so it's just a, just a physical mass of the hydraulic forcing of the water, pushing pathogens into the water and driving – then driving them through the surface or the groundwater to the point where you draw it.  It also increases things like turbidity in dirt, so when we do a sanitary – we call them sanitary surveys, as an old-fashioned term, but we still use it – of a water catchment, we look for pathogens sources.  We also look for sources of dirt and sediment and just stuff because that can overwhelm this infection.  And so you often get both at once, you get high pathogens concentrations and too much contamination, treatment plant can't handle it and then you get – so treatment plants have to be able to handle those wet weather spikes.  Often people will say, “Oh, it only fails when there’s wet weather.”  That’s the one time you don’t want it to fail.  So that effects design of treatment plants as well.  So it's absolutely right to focus on wet weather.

- And it is relatively simply as you have just –

- Yes.

- – explained in your response to the question.

- Yes.

- Is it easy to define a significant weather event?

- Well, I was just – I was amused by the – sometime the rainfall levels you get in parts of New Zealand, I think can be as someone was saying as high as eight metres per year, one of the people told me.  So if you were in South Australia where you get 450 millimetres of rain a year, 20 millimetres is a wet weather event.  You know, but if you are in other parts like the tropics, 50 millimetres – it's difficult to define it.  It requires local expertise and the other problem is have this concept of wet weather on a wetted catchment versus wet weather on a dry catchment, so if it's already wet, a 20 millimetre rainfall event can drive all this hydraulic flow, but if it has been dry for a few months that might all get absorbed into the ground and nothing will happen.  So it is really the flow that matters, not the rain.  It's the flow and the forcing that matters.  So we often use gauging stations with flow metres as a trigger rather than the rainfall itself as the trigger.

MR WILSON:

- So the mechanism is overland flow almost rather than rainfall of itself?

- Correct, it's the hydraulic forcing and the flow.  So people often talk about the flow in the river as the trigger for a wet weather event rather than the rainfall.  And the other thing is the rainfall station, we don’t have many rainfall stations, so you can get a local storm that is quite intense in the catchment and it will be totally dry in Hawke's Bay.  So you can actually miss it.  So it is important to consider that as well.  So the best place to – is to – and there will be tried, a link a link in the sanitary inspections will be done at the protocols for the – what we call selective abstraction protocol.  Some Councils have – they only draw weather – water when it's not flow.  We normally use a flow gauge rather than – or or something like that, rather than the rainfall and it's a trigger to stop taking water.  We normally try and use that as the link.

- But Dr Deere, the corollary of what you are saying, as I understand it, is that this contamination by Protozoa, by overland flow which is the root cause, can be of very short duration?

- Very short.  It can be, it can be a matter – I mean, we’ve had outbreaks and incidents with, you know, very – with short flashy storms of lasting for, you know, tens of minutes.  It can be very short.

- So even if were – one were to sample once a week for Protozoa or even in your example once a day for Protozoa, you could still miss the peak, you could still miss the incident?

- Yeah, so they're relying on sampling to manage microbial risk in food where you can batch it is fine but relying on sampling in a flowing water system is not fine.  So what the WHO has done for water with different from food is they’ve talked about microbial testing as being a verification of the past, of the history of what you already know as part of compliance, as part of checking.  They don’t use it as part of process control 'cos it's too slow.  We had – if we ask this question recently, we had a, again copying off the New Zealanders, the Australian utilities wanted to get a treatment standard similar to New Zealand’s 2005 and 2008 standard and so we’d use New Zealand as a model to build for the Australian version and we asked a bio-efficient, a bit like you’ve got Graeme McBride as your, probably your top water bio-efficient in New Zealand, the equivalent of him in Australia, we asked him how many samples do we need to be confident about a baseline cryptosporidium concentration given the variability, gave him some data.  He said you need hundreds, hundreds of samples and that’s just to get an average level.  That would still miss the peaks.  So microbial testing is overrated as a means of measuring risk and as a means of managing risk.

- But that is why the New Zealand Drinking Water Standards put the continuous measurement of turbidity as such an important means of compliance, criteria and compliance for coagulation, filtration processes and in particular the rapid changes in turbidity as being the focus.  So –

- Yes.  So –

- – how useful is that in groundwater sources?  Do you see an equivalent spike on turbidity, albeit it that turbidity will be, you know, a magnitude lower presumably?

- Turbidity’s a good indicator of growth contamination but it has two flaws.  So when we've studied turbidity spikes in wet weather events against pathogen spikes, there are two flaws.  One is that turbidity is usually quite a short-lived spike.  It might last a day or two.  The pathogens tend to follow on and they can be elevated for weeks afterwards.  Now, we've got, I can share them with you, you know, with the Inquiry but we've got some what we call polutagrams that show the turbidity spike goes up but the pathogens stay elevated for some weeks.  So you get a false sense of security.  When the turbidity goes down, the heavy stuff settles, the pathogens are still suspended in that, well it looks like clear water.  So it can be misleading as a lag indicator.  There's an upfront indicator when to stop taking water, it's not a bad indicator but the problem is in groundwaters, you can have faecal contamination, the example of septic tanks is a good example, where you can have very high-risk contamination.  You cannot see so we had a fatal outbreak last year in Australia from a septic tank transferring to a bore.  No indication from turbidity.  You wouldn't see it.  So it's a good, it's probably the best single best indicator we've got but it's not perfect.

- And what happened to the science of particle counting?  When cryptosporidium and Giardia first reared their heads figuratively, there was embryonic science that would suggest that you might be able to count these particles.  What happened to that science?

- Particle counting is still widely used on big water treatment plants and it's more used as a diagnostic tool.  The turbidity instruments are now quite reliable, will add, you know, the operators complain about them all the time but they’ve, in the scheme of things, they're quite reliable.  We've got a good experience worldwide of what levels of turbidity are relevant or significant and what levels take action.  The particle counters, that’s not the case.  They’ve got, what they're used for these days is diagnostics so if you’ve got a new filtration plant and you want to optimise the way you manage it, you use a particle counter to help do the optimisation.  They're not currently used in most cases as a routine management tool.

- Because you cannot maintain calibration on them?

- Correct.  They just don’t have, I mean, they haven't got the baseline, the background, the context but so they're quite common but they're usually there's one in the corner somewhere that’s brought out occasionally for diagnostics and optimisation rather than being a routine tool.

JUSTICE STEVENS:

- All of which means that describing a significant water event remains useful.

- Yes.

- Because you may well need to increase your testing following –

- Correct.

- – such an event?  Have you been helping, because the joint working group were grappling with how you define it, have you been assisting the District Council with input on that topic?

- Not yet.  I have been asked to look at some work that Tonkin & Taylor have done, making some recommendations on what they think is a reasonable trigger and professional judgment is often required to do that and so their local knowledge will probably be as good as anybody’s.

- It will be really helpful.

- But I will look at that.  My only comment to date has been to back up Dr Fricker’s comments and say, now we have got some good baseline data, let’s try and refocus the emphasis and priority on those events and back off a bit on the routine, just to give the lab some capacity and space to focus on doing what it does well.

- Thank you, very helpful.

CROSS-EXAMINATION CONTINUES:  mr gedye

- What is your assessment Dr Deere of the adequacy of measures to address Protozoa in the Hastings bores?

- On the bore that was considered to be at higher risk, there is a barrier for Protozoa which is the  -

- Across the road or –

- – the Brookvale 3 I think is the one that has the multiple barrier, the filtration, the UV.

- – yes that is Brookvale Road.  I am asking you about the Hastings bores, all the others?

- The other bores at the moment, they have done the same.  They have taken the same approach that the Canadian, the American, the Australian guidelines have taken which is to say we are not confident the Protozoa are managed, but they are a much lower risk than the bacteria in the viruses so we will put on, it is a grey area.  In the ideal world, you will have a Protozoa barrier on all the bores.  Because of cost implications, the pragmatic decisions that have been made by Health Canada, by US EPA and by the Australian Guideline setting bodies, they have said, at least managing viruses in the bacteria, the higher risk pathogens, because they are the smaller ones they go further in groundwater, they travel further, they are more likely to be there.  But the Protozoa are lower order of risk, they don’t cause a serious illness, they are not usually fatal in the way that the campylobacter, and salmonella and E.coli can be for example and they don’t go as far and transport as far.  So the pragmatic judgment has been for what you think are secure groundwater sources, just the extra barrier for the viruses and bacteria is enough, not the Protozoa.  That is a pragmatic judgment.  Ideally you would have a barrier of Protozoa as well but no jurisdiction I know of has made that decision yet because the extra cost.  Chlorine will take care of the bacteria and viruses, but not the Protozoa, so we have got that extra barrier required, extra cost required and so the way that is normally managed is to try and remove any obvious sources of Protozoa.  The difference in Protozoa is they come from – the humane factors of Protozoa largely come from a small number of sources is usually pre-weaned calves, pre-weaned lambs, humans.  There is some Protozoa in other animals that can affect humans but much, much lower levels.  And so you can manage those high intensity, high risk sources in the source .  What you are left with then is things like wild life, wild animals, adult stock animals, where the risk of Protozoa is much lower but you have still got the risk from the bacteria.  So pragmatic compromises trying to manage those at source with the Protozoa and then have the treatment for the pathogens but it is a grey area.  So what Council has done by putting in, on what they think are more secure bores, by putting in the chlorine barrier, they have been consistent with where other regulators in Health Canada, US EPA, Australian regulators and so on have gone but it is not the ideal world.  But there is a pragmatism required.

MR WILSON:

- Dr Deere have you looked at the current New Zealand Drinking Water Standards in terms of the energy levels required for UV, for Protozoa inactivation.

- I haven’t checked that no.

- Because we heard evidence in the earlier hearings that modern technology and modern understanding of the UVs effectiveness on inactivating Protozoa is such that it is now recognised as being more effective than was in the mid 2000s for instance?

- Correct.  Yes, that’s correct.  UV is very very effective on Protozoa.

- Okay, so again it would suggest to me that we have a situation here where we have got an out-of-date standard which doesn’t recognise modern technology and understanding of science, where there are, in fact, cheaper solutions for providing a Protozoa barrier than the current standards allow?

- Correct.  There is an excellent UV standard that dates to 2006 which is a US EPA UV guidance manual.  That is mapped to the German DV standards, are the two main global standards for UV disinfection and they show surprisingly low doses of UV killing huge percentages, you know 99.99% plus of Protozoa.

- But that would suggest that the technological development and the understanding of science means that providing that Protozoa barrier is now a lot cheaper than it was a decade ago.

- Correct.  That’s a fair statement, yes, and it's –

- So it may not be prohibitively expensive any longer?

- I think if you asked the microbiologists, they'd love to see the, the barrier.  If you look at pages 2 and 3 of the National Guidelines in New Zealand have this multi-barrier principle in there which is in the WHO Guidelines and most guidelines.  Under that principle, even if you’ve got what you think is a secure bore, ideally you'd put a UV plant on as well as an extra barrier just in case.  Because of the cost of that, the industries have tended to say okay, well, we want the extra barrier for the bacteria because that’s the one that might kill you so we'll have that in there and also remember the viruses 'cos they got the furthest in groundwater 'cos they're so small, well let the Protozoa off the hook.  That’s where the compromise has been.

- But if the cost comes down, it becomes a less difficult compromise?

- Correct.  Absolutely.

- Well, as –

- It's been purely a cost issue.  It's purely about the cost benefit sort of judgment about the cost benefit ratio.

- Can I rephrase that?  As the cost has come down, which is now a matter of record, perhaps we need to revisit whether or not that compromise is necessary.

- If it, if you asked the water scientist, they'd probably say put the barrier in.  It's a fairly small cost in the scheme of things but when you're dealing with hundreds or thousands of bores, lots of challenges to the community budget and the health department’s budgets, sometimes the compromises get made and so far the Anglophone countries have made a compromise where they’ve said the groundwater that we think is relatively secure, we'll leave with the Protozoa risk.  Dr Fricker, I didn’t read his statement in full detail but I saw a statement he sent very recently where he made a list of outbreaks of Cryptosporidiosis from groundwater supplies to make the points that it does happen.  So my view, my advice to Council is if the – if you're confident you're not anywhere near high risk sources of Protozoa, then it probably isn't worth it but these bores are very close to sheep grazing areas, very close to sewers.  Some of them are closest to pump stations and pressurised sewer mains.  You’ve only got what you can't see below the ground as a barrier.  In that situation I think you are at risk and because you can't see the barrier you can't see it fail.  There are Protozoa very nearby, within metres.  In that situation, if you could afford it, you'd put in a UV system for all the bores but it gets cost-benefit so it's easy for me to sit here and say that but, you know, it's, I'm not paying for it.

- Financial decisions?

- Yeah, that’s right.  I mean one of the things I was taught very early on as a water scientist by an experienced sort of retiring gentleman from, it was the chief scientist for New South Wales where I was working, he said to me, “All you can do is give advice as a scientist because the decision-makers have lots of things to weigh up and they may choose not to act on that advice,” and so, yeah, that’s all I can do in the situation as well, that if you’ve got sewers metres away from the bore, and you can't see the aquitard, you can't see the casing of the well in real time, then under the current best practice, you'd have to put a UV on because you can't see that process fail in real time.  Having said that, in terms of urgency, this is the point about urgency that Ms Casey made, because the Protozoa results today haven't shown Protozoa, and because the bores aren't evidently at high risk of contamination, you might put that as a, in the second category.  The chlorine would be the first priority to kill the, you know, the bacteria and so on.

- All of which demonstrates that there needs to be a strategy?

- Correct, and understanding and if you choose not to treat –

- And understanding where you are going to go in the short to medium term, which is your five to 10-year?

- Correct.

- That is the start point is it not?

- That’s right.  I mean many utilities right now I've seen in Melbourne Water, for example, one of the biggest ones in Australia, currently is dealing with that exact same question on one of their big supplies.  They're going to put a UV in.  When are they going to put in?  What will it cost?  Which model will they buy?  The risk is they think is tolerable in the shorter term but they want to get it in.  They’ve got that strategy in place and then they get the pricing submission, they get the funding for it and so on.  So that’s correct but the immediate priority is the chlorine and the immediate barrier.

- Thank you.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Talking about human sewage, the reading I've done has impressed me that it seems that the most numerous cause of outbreaks is human sewage –

- Correct.

- – as far as I can tell.  Does that topic justify an investigation in its own right?  Have you looked at sources of human sewage anywhere near any drinking water source for Hastings District Council?

- No but my comment on my first visit in April was I was surprised to see how close the drinking water bores were to sewerage lines from which were under pressure which is higher risk than those that aren’t under pressure.  Normally sewers things flow in, not out if they are designed properly.  As well pump stations that have high pressure sewerage and that physical proximity was unusual.  I have not seen that before.  I have only seen – generally speaking the bore fields, they accept there is going to be wild life in there, sometimes there is grazing but they try – because the utility owns both the sewerage and the water system, they tend to keep those, the bores well away from sewerage systems so that is something that the Water Safety Plan has to address and the process control tables that we are working on has to be addressed and the strategy for long term treatment has to say, well if we can’t reliably manage the risk in the sewerage system, and prevent transfer and can’t reliably measure the failure of the aquitard or the failure of the bore, we are going to have to put in a disinfectant system in, that can treat for those kinds of risks.

MR WILSON:

- And that risk, you could get a step-jump in that risk if you were to get an earthquake for instance?

- Correct.  So when we were looking at this question – when we adopted the New Zealand Standards in Australia, the treatment standards because you were about approximately 10 years ahead with the New Zealand Standards for treatment requirements, we didn’t recognise the secure groundwater standard, on the grounds that the groundwater experts told us that well casings fail too frequently.  You can’t see them fail, seismic movements, corrosion, pin hole corrosion, all these kinds of things.  You might have an annual camera inspection or some other pressure tests but it is not adequately reliable and so, as you say, if we said seismic events could fail that well at any time, we wouldn’t see it, then we wouldn’t have an adequate control.  We would be forced to find a downstream control.  The sort of thing that Mr Thew is talking about with his bow tie analysis could show that pathway and with a bow tie process you put in those barriers.  And if you say, we can’t put barriers in for the sewerage system because it is too old, it is underground and it might leak.  We can’t measure an aquitard failure, we can’t measure a coating failure, you would see that vulnerability and then you would be able to justify a UV system.  So what Mr Thew is doing, that risk pathway analysis helps to justify but if we can find we have got a highly reliable well casing, a method of detecting its failure adequately, you might not need to do that, so that is why we made that decision.

- But if you go back to your comment before where you said the Australians chose not to adopt the secure groundwater status that is embedded in the New Zealand Standards.

- Correct.

- If we were re-writing the New Zealand Standards today, “we” in the collective.  What would be your advice on continuing it, in the New Zealand Standard?

- As a microbiologist, I can’t recommend it.  So Health Canada in 2011, in their standards, Australian 2015 in their guidance, they both decided the secure groundwater could not be a generic simple default criteria that you can have.  So what they have both said is if you can get special dispensation from your health authority, to sign this off, that’s fine.  But as a default you must assume that even a secure groundwater at least needs one disinfection barrier.  That was what both the Health Canada and the Australian committees have come up with.  The US EPA is a bit less clear but they still push for, what they call four log virus which is basically a culmination process.  So New Zealand is isolated now in that respect, in having that category so easily achievable.  They talk about if you have got a highly geological survey, if you got special approval from the health authority and so on, you might be able to get away with it but that’s a special case.  And most small Councils are not going to be able to do that. And if you look at the amount of money and effort that has been spent trying to understand the Brookvale Bore that was the source of the outbreak, all that effort and we still don’t really know where the contamination from.  You can see that you can’t go bore by bore and do a $1M ground penetrating radar high hydrogeological models at that scale on any bore in the country.  It would be far cheaper and simpler just to treat it.

JUSTICE STEVENS:

- But isn’t that all, that made the case made even stronger by the fact that you can have an earthquake at any moment.

- Correct.

- And New Zealand, North Island, is particularly vulnerable.

- Correct. There is a hydrogeologist advising the Drinking Water Guidelines committee that I am on at the moment, he is on the committee as well.  He is a hydrogeologist from Flinders University and the hydrogeologist from SA Water, they both said the same said.  They both said, “When we go and look we find some big surprises in groundwater.  We find surprising rates of casing failures, either pinhole type failures or cracks or leaky grounds, leaky cable entries and we find surprising pathways” and the most recent incident we had in Katherine which is part of Northern Territory in Australia, we had a nine kilometre travel time from a – this is for a chemical not a pathogen – nine kilometre travel distance we were finding chemicals in bores nine kilometres from the site, which wasn’t obvious from the surface, and so –

- Are those papers that you have just referred to public available?

- Correct.  I can send all that information to the Inquiry, yes, absolutely, yes.

- That would be I think extremely –

- And they’re clear, they’re clear easy to follow documents, there’s no difficulty with those, they’re public documents, so to me the view of those committees, the hydrogeologists and the microbiologist committees and the engine – civil engineers has been we know you can have secure groundwater in theory, but to make it work in practice at a national level for thousands of drinking water bores in a simple guideline, it can't be done.  It just – it's not that simple, that’s the problem.

MR WILSON:

- And you wouldn’t differentiate between a groundwater source which has got a naturally positive artesian head and one that doesn’t?

- The problem with the using – relying on artesian head is that the aquifer is often penetrated by other things, that it can also have pressure, because if you have got thousands of other bores in the aquifer, and they can be pressurised, you can still inject things into that.  But certainly it is a much lower risk if it's got artesian pressure.

- But the recharge zone itself of course is prone to contamination?

- If the recharge zone, even if it's not prone to contamination, if you’ve got other contamination sources that could occur downstream, but it certainly if it is a pressurised aquifer and the recharge area is not subject to contamination, you got a much lower risk, but you still can't see local scale pressure effects and so for example there could be somebody with a well drawing water, they could for whatever reason pump things into that well and contaminate the aquifer, you can't see that. The problem we have got in hydrogeology is that most hydrogeological models are quantity models that are about yield and about water supply for irrigators and a few modellers have the sophistication to also put in solutes, usually sodium, or some particle and a very few modellers have also looked at pathogen modelling.  But pathogens don’t behave the same way as solutes.  They move differently from salt.  They’re bigger, they don’t go into the pores, so they actually move faster than the salt which is counter-intuitive, but they do, they move faster than the average salt.  The other thing is that most of those models have a scale where they might have a – and they have little nodes in the model that represent little nodes, they can be a kilometre apart.  The contamination can arise between places that are a few metres apart.  The model can't see that or represent that or represent that.  And they also usually have average or long-term time steps.  And yet microbial contamination can arise in a day or two, so a start of the art hydrogeological model might have daily or weekly or monthly time steps, it might have hundreds of metres apart where the nodes are, it's useless for microbial risk assessment.  Now, you can model at tighter scales and people do and they use super computers to do it, but that's not what is routinely done.  It's a highly specialised area of hydrogeological modelling that very few people can do or have done.  So relying on the aquifer where they use modelling or monitoring, the scale which you do that doesn’t match the time and the spatial proper scale of the microbial risk because short timeframes at small spatial scales, these modelling and aquifer management processes occur at huge spatial scales over long timeframes.  They’re not matched.

- I – from personal experience, I have modelled or had modelled circulation inside reservoirs and that is an incredibly complex piece of computing and you just think about a reservoir that is only a million gallons, you know, seven metres high and 15 across.  If you try and replicate that in the ground, I – you can understand exactly how complex it becomes and therefore how difficult.

- That’s right.  And also often there’s the lack of data to calibrate because you know from modelling, the modelling has to be fitted to something.  So no, it's an area that I think will improve in the future as we get more powerful computers and better data, but it’s – we’re nowhere near the point now where the hydrogeologists at the state of the art in Australia/New Zealand would be comfortable saying, “I can say that bore can't be impacted by that sewer or that sheep paddock.”  Because the spatial and temporal scales and the risk of failures can occur in-between sampling so if you think, for example, of five-yearly sampling is unhelpful to manage short-term microbial risk because between those five years anything can happen to that – to the condition of that water, it just doesn’t help.

JUSTICE STEVENS:

- All of which drives you towards the desirability of treating?

- Well, I – one of the criticisms of that comment is that we forget the catchments.  But the problem is if you want to manage microbial risk, although you don’t want to forget the catchment, you have to have some kind of timely monitoring on your process control and treatment gives you that, whereas the aquifer management doesn’t give you that timely management.  So unfortunately, it does drive you to treatment and I acknowledge that takes away from the principle of care, protecting the source and managing the environment, but if you were managing public health, you know, it's like saying –

- Well, they’re not mutually exclusive.

- They're not.  They're not.  Ideally do both.

- You do both?

- But unfortunately people tend to walk away from the catchment, so catchment management have criticised people for saying what I just said because they say they’ll walk away from the catchment and do treatment and my comment is but does the treatment works and we can control it and as you say, we can do both and the guidelines actually promote doing both but…

- And I suspect the RMA in New Zealand would drive you to do both?

- And that’s what the guidelines tell you to do but people, and it is clear, it's got the multi-barrier principle.  It talks about it on page 2 and 3 of the Guidelines which is about protect the catchment and do the treatment and then of course the network as well but unfortunately, people sometimes walk away from the catchment when the treatment is in place but…

MR WILSON:

- Well, I mean it is not uncommon practice in New Zealand to have catchment protection on surface water supplies, notwithstanding the fact that the treatment plant is perfectly capable of removing everything.

- Yes.

- Stopping it getting in in the first place so you do not have to remove it is a far better solution than, you know, allowing it to get in and then removing it.

- Unfortunately verbatim what other guidelines say, what you just said, that keeping it out in the first place is the priority but just in case it's there, you treat and the other thing is that some of the guidelines have, around the world say things like these guidelines aren't a licence to degrade up to the guideline.  You just still provide the best water that you can and manage all the barriers as best you can but of course when money is involved, those things tend to get compromised.

DR POUTASI:

- But what you are saying in the reverse is that any public belief in pure reliably safe untreated water is ill-founded?

- It theoretically sounds that you can have it but in a practical operational sense, it’s not, it's cheaper and more cost-effective just to treat it and assuming the contaminated than try and do the kind of, you’ve seen the amount of work done just for this one bore in this one incident to try and demonstrate the contamination pathway.  You can't do that for every bore in the country.  So from a practical point of view, I'm afraid the Canadian, the Australian, the US guidance committees have decided for a simple default national guideline, it's just too hard.  We'll recommend treating all supplies, even secure groundwater, but we'll give secure groundwater a lower treatment requirement but we'll still say you have to have the barrier, the multi-barrier.

MR WILSON:

- And the typical lower treatment requirement that they have compromised on is the Protozoa one?

- Correct.  They said you haven't got to pre-filter the water and you can just disinfect only, which is one less barrier and also we'll say we'll give you the Protozoa because if you think it's secure, that’s still the lowest of the three pathogen risks, the virus, bacteria, Protozoa, the Protozoa is the lowest of those three risks but that’s a compromise.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- In New Zealand, under the Drinking Water Standards, if your water supply is deemed or classified secure, you don’t need to treat the water.

- Correct.

- You understand that?  And one of the three criteria for achieving secure status is to have a water aging test?

- Yes.

- The rules that say that you need only do that once every five years, do you think a water aging test once every five years is an adequate criterion for achieving the secure status?

- Well, the short answer is no.  The long answer is that, which is just briefly, well, as brief as possible, there are two sides to that.  There's the baseline background risk that’s happening all the time every day and an infrequent test can give you an indication of that risk but there's also the spiky risk that you get when you get floods and storms and the one in five year test completely fails to take into account those.  So the one in five year test does tell you whether or not you’ve got constant continuous contamination of the bore or not.  You may not have, which is great for day-to-day risk but it's absolutely useless to protect you from events such as the one we're dealing with in this inquiry.  It doesn’t help for that at all.  It's a fundamental mistake to rely on that test to call the bore secure and that’s, I was surprised to see that five yearly frequency in that guidance.

- Well, the water aging test gives you a snapshot of one day –

- Correct.

- – when that sample was taken doesn’t it?

- At one location, yes.

- And the results frequently take seven to nine months to come through.  Do you consider that’s a problem as well?

- I think if you look at the long-term timeframe, there was a five-yearly test.  If the results take six months to come through, it's not a problem.  The problem for Council in this case was they had a test done before the incident.  The result came in after and that’s a bad look, so you know, in terms of it looks bad but if you, just want to get the baseline risk, it's still a valid test but it missed the acute risk.  So what we talk about if, there's a good paper from, and I might share with the committee from 1996, an excellent paper by the American Epidemiologist Floyd Frost, explaining this concept very clearly.  He's from the Centre for Disease Control in the US.  He did a nice diagram that showed in water you have the baseline we call the endemic risk and you can manage that by your five-yearly tests and your follow ups.  Then you have the epidemic risk, the outbreaks, the spikes.  You miss that with your baseline testing.  You’ve got to look – think about both risks separately and the treatment has to handle both.  So therefore the five-yearly test is fine for your baseline risk.  It's not helpful for your epidemic risk.

- Coming to more nuts and bolts, we will be looking tomorrow at what investigative monitoring programmes should now be put in place and how many samples, when and how to do it and I hope you'll be able to give some guidance on that but just briefly pre-figuring that, Protozoa testing in the Brookvale Bore, we've supposedly had 1000 testing per week per bore.  Brookvale’s had only five tests, five 1000 litre tests, none of which have shown anything.  What's your view of what Protozoa testing should be done at Brookvale Road in the future?

- Given you’ve had some negative results from your or is non-detects from your baseline programme, you would switch then to event-based and many people now only test Protozoa event-based.  The exception is the UK where the UK put in a daily continuous sampling process for legal reasons, the put in a continuous sampling process.  That was done for legal reasons because they couldn't sue the water companies without having evidence of contamination but everyone else in the world has gone for, as you’ve I suppose implied, you move to event-based programme.  Let's find out what happens in that bore after rain.  It may take you five years to get the result but we can find that out.

- And can you help on what rain means or what wet weather means?  Do you have examples?

- I wouldn't have the – I would be talking with a hydrogeologist and hydrologist to make that decision.  I wouldn’t have that expertise, no.

MR WILSON:

- Covered that before.

- Yeah.

- But from what you were saying, it is more about overland flow than it is about rain per se?

- Correct.  So it may be that it's just wet, been wet for a few weeks and it's winter and it's the ground’s wet and there's quite a small rain event could cause an overland flow event whereas in the – so that’s – it's more about the hydraulic forcing.

- So in the Brookvale case, you could actually put a measurement device in the side drains.  The point at which the side drains are starting to get wet, you are at risk.

- Your drains or it could be a level indicator in a test, in a sample bore, a piezometer measures the level of the groundwater when it starts to rise, then you're at – there's a range of techniques could be used.

CROSS-EXAMINATION CONTINUES:  mr gedye

- We've got a pond we could measure, the Mangateretere Pond.  And you'd apply that also to the Hastings bores, Eastbourne, Frimley, Wilson Road and so on?

- All the bores that I saw were reasonably close to pollution sources and so all the bores ought to have, if they're not going to have a Protozoa barrier, some very strong evidence they don’t need one and that would require, that’s hard to get that kind of evidence.  It's probably cheaper to put the UV plant in, in most cases unfortunately 'cos the testing is $1000 a sample but, you know, that’s, you’ve got – if you want to avoid testing, you want to prove you’ve adequate evidence, you're going to have to pay the money for the testing, to avoid treatment, sorry, you’ve got to prove.

- A sobering thought.  You wouldn’t have to do too many years of testing to surpass the cost of UV plants?

- Correct and that's, many Councils have gone for UV simply because for a small-scale system, modern UV plants aren't that expensive.  You’ve got all the extra security benefits.  For example, if chlorination fails but the UV is working, you’ve still got your UV barrier and you can keep supplying the water.  You’ve got double barriers.  So many Councils have gone down that pathway for that very reason.  If there an at-risk system they're not sure about, it's cheaper just to treat than try to understand the risk.

MR WILSON:

- Dr Deere, have you been keeping an eye on the developments in the Hutt Valley supply?

- No, I haven't, no.

- Because they have done just that.

- Okay.

JUSTICE STEVENS:

- What I was going to ask is, is it normal or common to see water sources near sewerage pipes and plants?

- I have to say I've never seen drinking water bores that close to sewerage assets before, even in developing countries, not that close.  I've seen them sometimes relatively close to septics within maybe 100 metres but actual live pressured sewerage assets literally on the same pad, I've never seen that before.  I was very surprised to see that.

- So that –

- And that’s one of the –

- – really gives context to your statement that this is a big risk?

- If those barriers fail and you can't see them fail, you’ve got a big problem.  Having said that, if they don’t fail, you're fine but it's just the fact that you can't see them fail so if a modern water safety plan is required timely detection of barrier failure and because you can't get that with aquitards and casings, you end up being pushed to treatment and that’s just the way we manage the risk these days.

mr gedye ADDRESSES THE COURT (12:55:22) – convenient time

WITNESS stood down

inquiry ADJOURNS:	12.56 pm

inquiry RESUMES:	2.02 pm

WITNESS INTERPOSED

MR GEDYE CALLS

JAMES PALMER (SWORN)

JUSTICE STEVENS:

- Good afternoon, Mr Palmer.  Sorry to have detained you but I know you have been in and out and have been following the proceedings but we are very happy to interpose you now so that you can meet your other engagements.

- Thank you.

CROSS-EXAMINATION:  mr gedye

- Mr Palmer, I just want to ask you a few questions about the joint working group and I appreciate that you haven't been to the meetings and that Mr Maxwell can answer questions about the meetings, but from your perspective, what's your view on the terms of reference for the joint working group?  What do you think they should contain and where do you see the terms of reference going?

- Right.  So look, as I understand it, at a meeting in December of last year, the terms of reference which had been developed with some haste were adopted by the joint working group at that point in time.  Since then obviously we've had the findings of stage 1.  The terms of reference as initially drafted in my view were relatively broad, although they did have a particular focus on the most pressing matters.  I think stage 1 has identified perhaps a broader range of matters that go beyond the immediate issues with respect to the supply at Brookvale Road and I'm particularly thinking about the aquifer-wide supply.  We do have Napier City Council participating in the JWG for example and so I think what we now need to do is just to test whether or not the terms of reference are appropriate and durable going forward because it's the view of the collective chief executives of the local authorities in the region that the JWG has merit in being essentially a standing body that will have an ongoing role in ensuring the collaborative approach to the management of drinking water supplies across the region and in addition to that, we are proposing that there be a joint committee under the Local Government Act be established of Councillors from each of the five Councils, the DHB and Ngāti Kahungunu Iwi Incorporation to oversee the joint working group, ensure that it has an escalation path and that there is political, a governance and accountability over the top of the joint working group in a statutory construct.  So that can be enabled today under the Local Government Act, Schedule 7.  We do have experience with that in the region with our coastal hazards joint committee of Councils and so what I think we also need to do is once we've established that joint committee, and I think it'll take us about two months to get all of the Councils formally agreeing to adopt that approach, is to give that governance body the opportunity to also reflect on the terms of reference and add in anything that they also feel is appropriate.

- Quite a few things arise out of that that I need to clarify.  We've had a draft document, I think drawn up by Ross McLeod, which is called a terms of reference and it's a sort of charter or governing document and you're aware of that document?

- Yes, I am.  So Mr McLeod and I have discussed that within the last week or thereabouts and there are some refinements going onto that so the one I have in front of me, which is a working draft, relates to that joint committee of Council.

- So it's not actually a terms of reference for the JWG itself but rather the next tier up the, what shall we call it, a CDOs committee or?

- Well, it would be of Councillors so it would be Mayors and Chair or Councillors.  We are proposing there be two elected representatives from each local authority on there and look, the reason we're focused on that is, as I said at the outset, there is a already agreed terms of reference for the JWG that was adopted in their minutes and I believe it is part of the evidence that’s been provided to the Inquiry back in December and I do appreciate that we do need to revisit those terms of reference and ensure, particularly with the findings of stage 1, that they are fit for purpose and that’s something that Mr McLeod and I are currently advancing and we propose to bring back that revised terms of reference to you in August if that is appropriate.

JUSTICE STEVENS:

- What your answer has flagged is the reason why you are working together to bring representatives of Councils into the mix.  I am certainly interested in the rationale for that and I mean obviously the existing legal framework allows you to do it.  You do not need any permission from us or anyone else to do it.  It is purely voluntarily, so there are no structural limitations and obviously it is something that is consistent with other work that is going on in the region.  So for all those reasons, it seems wise.  Do you want to elaborate on any other reasons why this governance layer is thought to be necessary?

- My understanding, Your Honour, is that this was initiated initially at the behest of the Mayor of the Hastings District, the chairman of the Hawkes Bay Regional Council and the chairman of Ngāti Kahungunu Iwi Incorporation.  So they were having dialogue earlier this year about the need to work collectively at the political level to ensure that the Councils and the DHB and iwi to the extent they can are working collaboratively.  I think by having that political governance that ensures that is the case at the highest possible level and that there is transparency and accountability around that.  I think it helps to provide the joint working group, which is very much at the technical level, to have an escalation pathway, particularly where there may be some disagreement or some difficult choices to be faced and I also think it enables the political leaders of the region to go to the community collectively with some of the challenges that lie ahead and I think if you consider the debates around treatment and the community’s sentiment in that regard, it would be better if the institutions of the region that have a collective responsibility are aligned in their thinking around that and are able to front the community collectively, if you like, rather than be picked off one by one or have different views which would probably destabilise and undermine a constructive dialogue with the community on that.  So yes we have got a statutory ability under the Local Government Act to form such a committee.  In our submission, in my report to you, the submission made in the last week, we did however highlight the fact that while that committee can come together and can make recommendations for Councils to take forward.  There are genuine limitations in terms of the other processes, particularly under the Resource Management Act.

- Of course.

- That need to happen and they will involve public input and other judicial processes et cetera.  So just to really be clear that the joint working group cannot unilaterally come up with a set of arrangements and enforce them, if you like.

- But what it essentially is doing is ensuring that there is not a disconnect between the political level and the technical working level?

- Look absolutely and I think we all learnt through stage 1 of the Inquiry that our governors were not adequately informed around the risks and the issues related to drinking water and that that was not an acceptable state of affairs that we now seek to remedy.

- Well, that has been really helpful because possibly something that we had not focused on quite as much as you have now illuminated, so that is really appreciated.  Just let me check with my colleagues.  Dr Poutasi, do you have any questions arising on that topic.

DR POUTASI:

- My only bit, and I think I can imagine the answer but perhaps it would be good to have clarity, how do the CEs therefore fit into technical working group, political governance?  Where are the CEs?

- So the CEs are likely to be a first line of advice, if you like, to the elected governors.  We have our own mechanisms as chief executives to meet regularly on regional issues and we tend to do that informally but regularly.  I think one of the things we have reflected on, and the five of us did meet last Friday, is there are some new appointments.  I've obviously just arrived recently, as has the Chief Executive of the Central Hawkes Bay District Council.  We've reflected on the Havelock North incident and the need for us to work on a more regular and continuous basis as a group so that will be happening in parallel and I guess in terms of the structure, we would be very much involved with the joint committee’s deliberations and work.

JUSTICE STEVENS:

- I suppose, just picking up on that, the membership of the technical level might not necessarily be a CE.  It is possibly more likely to be at the level of Mr Maxwell for the Regional Council and Mr Thew.

- Look, I think that’s correct and I think there's a limit to how much value chief executives can add to the very specific work of the joint working group and I think our particular role is ensuring that our governors are well cited on the issues and that our staff are adequately resourced and supported to do the work they need to do.

- So the terms of reference are now focusing on this governance layer?

- Certainly the terms of reference which we're seeking to finalise are for that joint committee and we will need it to be formally adopted by each of the five Councils in order to have undergone the necessary Local Government Act processes to become an official joint committee under the Act.

- And do you anticipate that it will be possible to advance that far enough so that we can at least be informed in the August hearings about progress and hopefully have it resolved because if and to the extent that we want to recommend this as a useful model for other parts of New Zealand, all the good work that you are all doing would be very valuable to us.

- Yes.  Mr McLeod and I are seeking to finalise this terms of reference within the week or thereabouts and to commence the process across the five Councils of having it formally adopted.

- Wonderful, thank you.  Mr Wilson?

MR WILSON:

- As I understand it from what you have been saying, this is a joint committee of the five local authorities in Hawkes Bay.  So that includes –

- That’s correct.

- Whereas at the moment the joint working group does not include Wairoa or Central Hawkes Bay?

- That is correct.

- So is the intention that they subsequently join the JWG?

- So in all likelihood, and it will depend on the work programme of the JWG, Mr McLeod and I are both of the view, as is our colleague at the Napier City Council, that our most pressing issues are in relation to the Heretaunga aquifer and that is particularly because of the lack of treatment or historic treatment that has occurred there.  The water, drinking water supply in Wairoa and Central Hawkes Bay is currently treated and so we see while there are ongoing drinking water management issues that we will want to attend to in those areas, they are less urgent and I guess what we're seeking to do is ensure that the learnings by the bigger Councils in the region are leveraged to the extent possible for those smaller Councils and that we are actively working as a region to assist Central Hawkes Bay and Wairoa District with managing their challenges as well.

- And being a political oversight committee, for want of a better description, the tenure of the individuals to this committee can only be for the current triennium?

- That’s correct.

- So you will need to reconfirm the purpose of the committee and the joint committee and reappoint people subsequent to the next Local Government election?

- That is correct.

- And would you at the same time anticipate that you would formalise it as part of the tri-annual agreement?

- Absolutely we would.  Currently the Coastal Hazards Committee that we have as a joint committee is contained within the triennium agreement and there we have been through an electoral cycle and there has been a relatively high degree of continuity, given the tenure that local government elected representatives tend to have.  We don’t envisage that to be a particularly difficult issue to manage in terms of institutional knowledge across different electoral cycles.

- I think you here yesterday when I asked Mr McLeod and Dr Snee the question about continued commitment five to 10 years down the track.  What is your view of how that is best managed?  When everything is tickety-boo on the water supply, there has not been an incident for years but there is still a black swan just over the horizon, how do you manage to ensure that commitment?

- Look, I don’t think there's a silver bullet to that.  I think there's a whole range of things that would need to be in place to ensure it and I'm sure that the Panel in its deliberations will consider how all of those cumulatively create the right incentives.  I do think that the terms of reference for both the governance group and the JWG needs to explicitly have an ongoing performance monitoring and evaluation function to ensure that there is no degradation from a range of interventions that may be put in place over time or that commitment slides away and I think if that’s clearly in there that there is an ongoing imperative and an ongoing need in those terms of reference, that will be important.  I think also the national guidance by way of both on the national environmental standard and the national standard under the Health Act, I think if they are more explicit about that imperative around ongoing monitoring, that’s important as well.  One of the things that I am placing some emphasis on in my organisation presently is our role of ongoing risk identification and risk management and I think if the best practice around that is adopted across the local authorities, this will be an issue that one would hope never falls off a risk register because of the nature of very very small deviations in system performance having very large consequences and I think that’s one of the really big shifts for us and potentially for the sector, the local government sector and particularly Regional Councils, is recognising that our risk management approach that we typically have for environmental management where you can I guess allow for a few fish to die in a lake for example if most of them are well, is not acceptable in a public health context where, you know, one death is unacceptable or any significant transgression, so there's a shift, if you like, in our risk identification, our risk management, our risk appetite that needs to take place to having very very low tolerance for risk when it comes to public health matters.

- In other words, you might paraphrase that to say we now understand the consequence, the end of the risk formula, perhaps a little better than we did before?

- Look, I think that’s absolutely true and I am, I publicly committed recently to reviewing the compliance functions at the Regional Council and I think to be fair to that small team, they have – and you know that there are 8000 registered bores in the region, they have two million hectares of land to be responsible for and thousands of consents, so historically they have taken a very targeted approach and I don’t necessarily think the public health has been a high enough on their risk assessment, I don’t think low probability high consequence matters necessarily had the attention and then I think where other public institutions are involved with holding resource consents, compliance has been assumed, if you like, based on their capability and capacity and again I think that is something which has been shown to be an unreliable basis on which to target compliance effort.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- In terms of this governance committee, Mr McLeod’s draft provides for an independent chairperson.  Is that something you think is desirable or necessary?

- Look, I think it is desirable and it is desirable because there is no, there is no hierarchy, I guess, and I think one of the – within the local Government, there are different roles and responsibilities and I think some of the tension goes to different perspectives around whether there is a hierarchy or not and I think one of the things that was borne out in Stage 1 is the multi-barrier approach does not really assume that any one agency is more in charge than the other, everybody is equally responsible and has an equal role and I think an independent chair will reinforce that.

JUSTICE STEVENS:

- While respecting the different interests of the various parties that make up that group.

- Absolutely.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- How many members would be on this committee, I may have not listened to you properly, but how many from each Council and from the iwi?

- So it's proposed two, including the iwi, so that’s five Councils plus the DHB plus the iwi, so that does take you to 14 which is a relatively large committee, I accept, but Council committees are typically of relatively large numbers and that is not too far off what we currently have with either the Regional Transport Committee which is another example of a statutory joint committee or of the Coastal Hazard Committee.

- So the DHB is also going to participate as well as the Councils?

- Yes, correct.

- And that will be elected members of the DHB Board, will it?

- That’s what’s envisaged, yes.

JUSTICE STEVENS:

- What this is showing us is that there are some areas within the region that even though Councils don’t have a mandate to merge, nevertheless the specific tasks are best dealt with on a regional basis.

- Absolutely Sir and I think there has been a clarity in some of those other examples about the level of interdependence that the Councils have and the level of overlapping jurisdiction and I think prior to the Havelock North outbreak that level of overlap and mutual interdependence was not appreciated to the extent it needed to be.

- In the water space.

- Correct.

- But we’re getting there with transport, getting there with – in other areas, but now the impetus is there for water?

- That’s correct.

- Drinking water.  Sorry, Dr Poutasi?

DR POUTASI:

- I was merely going to say I – is there a desire to constrain the District Health Board in whether it points appointed or elected members?  You were reaching for just elected, whereas of course, a District Health Board has a joint  –

- Has joint – well, look, I think it's governance level and I think it doesn’t so much matter whether it is an appointed member, it needs to be somebody at that governance level representing the highest level of interest that the DHB has.

- Well, itself would make the choice as to which of it's Board members.

- That’s correct.

- So yes.

JUSTICE STEVENS:

- So flexibility and choice could be important.

- Indeed.

- Not to hamstring – yes.

- Absolutely.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- And if you had an independent chairperson, would that obviate the need for the JWG itself to have one?

- Potentially on the basis that the escalation path of any disagreement is through that joint committee, so you have another means for reconciling that if, indeed, that is part of the role that Mr Tremain has been providing and I don’t think he has needed to do an awful lot of that because there has been so much commitment and goodwill to working together, but obviously in the years ahead there will be difficult choices around where costs fall and what regulatory impositions need to be made.  I don’t have a strong view in this and having not participated in the Joint Working Group I would take advice from those that have been there, but look, I think independent facilitation of these processes when there are multiple agencies that a lot at stake has – generally has a high degree of value.

- Yesterday we did not appreciate, I think, that there was in fact a two tier system in the offing and I am just trying to understand more about this.  We discussed yesterday quite a lot about the terms of reference for the JWG and what it was and was not and what its purposes would be.  Would those matters now be set by this governance committee, effectively as a work programme or as something like that?

- Certainly in the medium to longer term we would anticipate that that joint committee would set both the work programme and the terms of reference for the JWG.  Recognising that it may take a couple of months to go through the Council processes to establish it and Mr McLeod and I have discussed in the last 24 hours, the desirability particularly in relation to your timeframe, to possibly revisit both the work programme and the terms of reference for the JWG prior to the joint committee of Council being formed and that is really just to keep matters moving along and then subsequently revisit it once the joint committee has been established to test whether or not it does meet with their satisfaction.

- I think that there is quite a bit of evolution to be done before the August hearing and beyond because this joint governance concept is very obvious in this region but in smaller regions with only one Regional Council and one District Council, query whether joint governance group would have the same role and I think –

JUSTICE STEVENS:

- Or be necessary.

- Mhm.

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- If that is a worthwhile thing across New Zealand to be thinking about.  Another observational question is until now the JWG really arose via the Inquiry and the outbreak and has really been looking at HDC’s water supplies and I understand Napier attends really more as an observer.  Is what you are now talking about really going to throw open for the JWG, all drinking water safety issues from Central Hawke’s Bay, sort of Dannevirke or wherever it stops, right up to Wairoa, the whole region?

- That’s correct and therefore challenge is, how do you eat the elephant?  And so there is a degree of prioritisation required in the work programme and some risk assessment underpinning all of that and I think that underscores the fact that this joint committee probably has a relatively, a long tail of work ahead of it and it is all the more reason that the collective resources of the region be applied to managing these issues and that essentially if there is a drinking water quality issue in one of our or less resource parts of the region and it could even be a small community, that there are the collective resources of the region to potentially be drawn upon to respond and assist that community.

- Another item on the agenda for August is the question of some dedicated water authority or a special purpose entity.  Would you have any comment on the proposition that this sort of joint governance committee could become a sort of quasi water entity, speaking very, very broadly, that might start achieving things like group laboratory access or consistency in standards and processes or purchasing power for UV plants and any sort of matter that affects the safe supply of drinking water across the whole region?

Absolutely I think is the simple answer.  I did read the transcript from yesterday morning and while I was not present, I did note that Mr Tremain did refer to the amalgamation debate that has occurred within the region.  I think it is fair to say that that debate illuminated some of the benefits of economies of scale and of a region pooling its resources for better outcomes.  It was also clear the community wanted to retain a high degree of representation at community level and in the end on balance, the community felt that that was the more important imperative, was retaining that representation.  I think it's fair to say that all of the Councillors across local government in the region and certainly Councils officers are acutely aware that there was also a large number of people in the community that did want amalgamation and did see benefits from it.  So if anything, we've been thrown the challenge to therefore deliver on what benefits can be accrued through collective effort wherever possible while also retaining that degree of political representation at a smaller scale.

MR WILSON:

- Mr Palmer, are you familiar with the Wellington Water Limited model?

- At a very high level I am, yes.

- Do you see applicability for that sort of model in Hawkes Bay?

- Potentially.  I guess one of the challenges in the Hawkes Bay region is we don’t have, while we have the Heretaunga aquifer, we do have other supplies that are spread across the region, so we're possibly not as collectively dependant on common resources to the extent that Wellington is, although I appreciate in Wellington there are, there's a diverse range of suppliers as well.  I think we’d need to do a fair bit of analysis to understand what the benefits would be.

- Have you followed the debate with the Waikato Water?

- No, I have not.

- I suggest you might because that’s much more akin to the model, to the geographic and distribution that you are seeing here in Hawkes Bay.  Three local authorities there propose, Waipa, Hamilton and Waikato District.

- I do make the observation that retaining a degree of control and oversight politically and by management of Councils, if indeed that is undertaken effectively, may be an important element of managing risk around water and I guess the devil is in the detail with such models and the extent to which the management of drinking water is outsourced to a for profit institution or outside of the direct line of sight and control of Councils is just a risk that needs to be weighed in those considerations.

- And neither of those have occurred in either the Wellington model nor the proposed Waikato model.

JUSTICE STEVENS:

- I guess what Mr Wilson is alluding to here is that the model that joint working group and the Councils in this region are exploring is not the only model.

- Understood, Sir, and look, I do think that as the joint working group undertakes it work over the next few years, those opportunities for consolidation, common management, if you like, of assets will probably rise to the surface because it will become self-evident that there are weaknesses within the system and there are strengths within the system and how do we minimise the weaknesses and maximise the strengths that we have.  So that could well be an inevitable evolution.

- And part of our work in stage 2 is summarising relatively briefly the two models that Mr Wilson has adverted to.

- Understood.

- So your ongoing work is appreciated because (a), it's something that you have come up with from your own initiative and does not require structural change.  It is, obviously on current indications, something that is suited to the area and it is social and geographic and other interests and will provide an alternative?

- Yes.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Would the outcome of this governance committee be that the JWG as we currently know it will become quite a different animal and that it will be looking at matters from Wairoa to Central Hawkes Bay and probably wider and bigger matters and that it may have more members and be quite different from what we're now seeing?

- Possibly over time and I think given what we need to work through with the Heretaunga aquifer in particular, both in terms of understanding the groundwater and its relationship to the drinking water supplies and remedying the situation, with the Brookvale situation, we've got quite a lot to work through yet.  It could well be that the joint working group would have a subcommittee working on Wairoa that would be led by Wairoa, if you like, and they may benefit from having science staff from the Regional Council, having engineering staff from Napier City or Hastings District helping them with all of that and I think it is just in the spirit of regional collaboration where I certainly see a benefit lying.

- For example will the joint governance group be involved or address the question of the consent of Brookvale Road in May ’18. Will that be a significant matter which it will manage and try and work through jointly?

- I would expect that at the governance level, there will be a desire to see much as the panel has discussed in the last day or two; a desire to see a strategy and for  them to understand what are all the constituent parts that need to be aligned and what is the programme of work going forward, so it is hard to see them having a focus on anything less important than that in a sense.  So they will want to know what the plan is and indeed when we look at the coastal hazard example as a parallel, it is very much around what is the plan over  the coming short, medium and long term and what are the infrastructure implications et cetera.  So yes I would see them wanting to oversee where Brookvale goes.  Obviouisly there will be statutory processes that will need to be kept independent if you like of that and the joint committee may well make some collective recommendations but the consenting authorities would just need to be careful and certainly in the case of the Regional Council that we don’t compromise those processes at all.

- No of course.  Do you have some sympathy for the idea that the workings of the Joint Working Group should be public, the minutes and so on should go on a website, with the transparency being important?

- I certainly see transparency as being important and I have no problem with their operations and I think particularly their reports, their minutes and what have being made publicly available, I think that is helpful.  The joint committee of Council, we would anticipate unless it has a particular matter, it needs to go into committee, would meet in public and I think at that governance level, that is where the greatest imperative is, in terms of public interface and engagement.  Joint Working Group in many respects is at the technical level and I suspect the public has a lesser interest in the minutae if you like of the issues and far more interested at the more strategic level.

- Would you expect this joint governance committee to lead to greater consistency across the region, for example in where the water is treated or not, not naming names in any particular Council?

- Well I think common practice will evolve through common endeavour and I think both as I mentioned before at the political level, it is helpful to have a shoulder to shoulder approach and look that was part of the philosophy that led to the joint committee around coastal hazard on the basis that if one Council in a neighbouring jurisdiction takes a particular position with a community that differs from that which another Council does, it is very difficult for those Councils to maintain that position, so I think to that extent yes, we would see a more common approach taken.

- If I can just come to the more nuts and bolts matter of the White paper.  I think you are aware that the Inquiry’s recommendation to pursue aquifer investigations was, I think, in the April meeting referred by the Joint Working Group to Rena Douglas to prepare a White paper.  Could you just tell us about what this White paper process entails and what is going to happen and in what timeframe with it?

- Yes I can.  There are actually two White papers.  So recommendation C and D are being treated through two separate White papers but that is a matter of detail.  Ms Douglas, we had hoped for her to be present today to observe these discussions but she is interviewing members of the JWG this very day and has been on an intelligence gathering exercise for writing those matters.  She completes all of those interviews with all of the participants across all of the relevant agencies by the end of this week.  She is then distilling that into working drafts of the White papers.  Now she had been working to a December deadline.  We have discussed with her overnight the prospect of bringing it forward.  She is travelling overseas at the end of July to a family wedding for the best part of August and so having conferred with my colleagues we have determined that in the interest of assisting the Panel in its work, we will supplement the resource to take the work that she has completed close to her departure and ensure that it is finalised and available to you for the August hearings.

- Thank you.

JUSTICE STEVENS:

- Well, thank you, that is really, really appreciated.

- Understood.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- When you say “recommendation C” that was that the water safety JWG members notify each other and keep each other informed of any information that could affect drinking water safety risks.  One can take that as a simple operational matter that you must keep each other informed, but do I take it that this is now being pursued in terms of identifying all information held by agencies and compiling databases or libraries of this information so is recommendation C the information piece that you are pursuing?

- Yes, it is and the intention will be to ensure that there is a collective understanding about the information that is available, the information that is required and that there be a framework instead of protocols around the exchange of that information and, I guess, a monitoring in place to ensure that that framework is implemented and that we can have confidence that where information is gleaned that it is shared in a timely manner to the right people.  So it's really putting some structure around what has been a very informal set of arrangements that were observed in Stage 1.

JUSTICE STEVENS:

- That rather suggests that that recommendation could be split into two parts.  One which sets the objective of information sharing –

- Yes.

- - among members of the JWG which should remain.

- Yes.

- And secondly an information gathering part which is within the work being carried out by Ms Douglas.

- That sounds perfectly sensible, Your Honour, so I am happy to reflect that back to her as the author.

- And I think once we have heard from all of the people speaking to the reports we will spend some time tomorrow just fleshing out any possible variations to the recommendations.

- That would be very helpful.

- Because we appreciate that as time goes on, some of those recommendations, in a sense, have exhausted themselves or alternatively have been developed and interpreted in different ways and we just want to keep them current.

- Thank you, understood.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Just by way of fleshing that out, the recommendation to keep each other informed, I think arose at a very workaday level from some of the examples we saw in Stage 1 where the Regional Council was granting Te Mata Mushrooms certain consents, I think virtually in the same week or fortnight that the District Council was granting other consents.  That is one example of keeping each other informed of day-to-day things happening.  Another, of course, was the E.coli event in October ’15 at BV3, no one actually told the Regional Council, it read about it in the paper and there was a few emails and I think what started off recommendation C was simply at that workaday level that members talk a lot and tell each other what's happening relevant to water, so that is a recommendation I would envisage would just remain because it is no more than commonsense, really.

JUSTICE STEVENS:

And can continue.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Indeed.  I think the key to it is putting the structure around it so that it is not left to relationships that may or may not exist between individuals.

- Yes, because people move on.

- Exactly.

- But what has come out of recommendation C which I must say I hadn’t contemplated was basically building up a database or a library of information or access to it?

- There has been an ongoing discussion about whether or not we do build a database.  I – prima facie it has some value.  My slight hesitation is that there is potentially an awful lot of information involved here and I wouldn't want the efficient and effective exchange of information between institutions to rely upon a major IT build, or if you like that everyone was then dependent on.  Common source information, I think, is valuable and possibly we need to look at the inter-operability of systems and information exchange that exist between GIS databases within Councils, for example, that may have wider co-benefits beyond just drinking water supply.  So there is a lot of issues in there that we need to explore and I do think the most immediate imperative is to ensure that relevant information is being exchanged and shared proactively and what the best infrastructure is to support that is something that we will need to work through over time.

- Yes, so I used the word database in haste.  I'm aware that once built, they take an awful lot of maintaining and there also is the question of the WINZ database, a new version of which is just under development and that is a database with dedicated drinking water data in it.  So you wouldn't want to duplicate that or interfere with that either but I don’t think the Inquiry proposes to get involved in the mechanics of how that information is shared.  I think we just need to end up with a recommendation in high level terms that the members, and it might go along the lines, extract all information relevant to drinking water and make it available or list it, something along those lines and I think counsel are going to confer tomorrow morning to find some wording that would work because of course there's –

JUSTICE STEVENS:

- We would appreciate it to the extent that you and Mr Matheson or Mr Maxwell and Mr Matheson can assist with what you see as practical because we would like to support and encourage the work that Ms Douglas is doing.

- Yes.

- And to the extent that it is useful on a broader basis, well then we will have it available to consider.

- So look, I think that the greatest benefit you can add for us on this very specific matter is clarity around the information that you believe should be collected and should be exchanged.  The nuts and bolts, if you like, of how that’s undertaken I think is appropriately worked through and I just would draw the Panel’s attention to the fact that we do have a shared services company between Councils in the region which we are all shareholders of and the chief executives all sit on the board of directors of and that has a large programme of shared services around IT products, finance, legal, HR, you name it.  There's a whole range of things that we're constantly working on to do more collectively to provide efficiencies and greater effectiveness.

CROSS-EXAMINATION CONTINUES:  mr gedye

- That’s that company called?

- HB LASS.  Local Authority Shared Services.

JUSTICE STEVENS:

- You can add that to the joint transport committee and the coastal hazards committee.

- There is a –

- As a shared interest group.

- Yes.  Look, there is a lot of collaboration occurring within the region right now and I think in many respects the Havelock North incident has been probably more a feature of past orientation than it is a contemporary one and probably drinking water was just an area that hadn't caught up with the rest of the programme in other areas where we're far further down the track.

CROSS-EXAMINATION CONTINUES:  mr gedye

- The final point on the joint governance committee, would you see this then extending to the Three Waters?

- So the discussion that Mr McLeod and I had with our colleagues on Friday was that we felt that this should focus on Three Waters to the extent it has an impact on drinking water at this point in time.  So where storm water or wastewater poses any kind of risk to drinking water, it's very much within scope.  However, the more generic management of those is a matter we thought we would come back to further down the track when we had more confidence that the drinking water issues were well and truly in hand.

DR POUTASI:

- The only thing I would add, and again it is self-evident I guess, but the vehicle that you just described, you know, the joint vehicle that at the moment of course would not include the District Health Board because it is local government or it does?

- So our intention is very much to have them at the table and there's no problem with them being added in.  The mechanism is principally around Councils being able to work together.

JUSTICE STEVENS:

I have no further questions but I am really grateful that you have been able to help us in the ways that you have.  Just let me check with other counsel.

QUESTIONS ARISING: Ms RIDDER – NIL

QUESTIONS ARISING: Ms BUTLER – NIL

QUESTIONS ARISING: Ms Casey – NIL

QUESTIONS ARISING: Mr Matheson – NIL

MR PALMER:

Your Honour, if I may, could I just please convey the apologies of my chairman Mr Graham, who had wanted to be here today.  He understands the importance of your deliberations, it was a matter of having Council meeting today that he was not able to attend.

JUSTICE STEVENS:

We appreciate that the work must go on and we are grateful that he is continuing to do it.  And you will just be available as required to help with the tweaking of the wording of the recommendations, thank you.

WITNESS EXCUSED

JUSTICE STEVENS ADDRESSES Mr Gedye –Order of appearance of witnesses

Mr Gedye calls

peter wood (affirmed)

JUSTICE STEVENS:

- Good afternoon, Mr Wood.

- Thank you.

- Sorry to hold you up, but as you can see, the work that we are doing is really important.

- Yeah, absolutely.

- And we are making excellent progress, so thank you for waiting.

CROSS-EXAMINATION:  Mr Gedye

- Mr Wood, perhaps we could start with the Joint Working Group and you attend those meetings, don’t you?

- Yes, I do.

- Have you sat through yesterday as well?  I am sorry, I don’t know what you have listened?

- I got most of yesterday, so.

- Well, I wanted to ask you similar questions about the Joint Working Group.  Having attended it, has it met your hopes and expectations for what a Joint Working Group would do?

- I think as a group that was set up to meet the required or meet the recommendations and conduct a work plan based around the recommendations of the Inquiry, yes it has, it has certainly been very good.  We – it started off being very focused based on the recommendations that came through.

- You have heard just now the proposition that the Councils are working towards a two-tier group with a governance level.

- Mhm.

- With the JWG being then more of a working group.  What do you think of that structure?

- Well, I haven’t really given it any thought until about an hour ago.  The – I know that we’re having similar meetings about how we would set up collaborative groups in other areas of the country, given what has already happened.

JUSTICE STEVENS:

- “We” being Drinking Water Assessors?

- Drinking Water Assessors with District Councils and Regional Councils in say mid-central area which I generally deal with.

- So that includes, what Palmerston North?

- So the – its Horizons Regional Council so what has happened is we have had initial meetings between the Drinking Water Assessors and Horizons Regional Council.  We have then had – the Horizon Regional Council has had a meeting with all the chief executives including Mid-Central District Health Board Chief Executive and we have got agreement from chief executive level for information sharing and so we have started down the track of sharing the information that we have around water supplies with Regional Council on the basis that all the chief executives have signed up to that.  Now that’s seven local authorities.

- And includes, who?  Palmerston within Horizons?

- So that’s Horowhenua District, Palmerston North City, Tararua District, Manawatu District, Rangitikei District, Whanganui District and Ruapehu District.

- Thank you.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Having heard about this two tier structure, would you have concerns that the DWAs wouldn’t be directly represented at the governance level?

- It is a very difficult question to answer.  At the moment, because I am employed by Mid-Central District Health Board, the governance of Hawke’s Bay District Health Board, I am separated from that to a certain extent.  Now having said that, I think we are working very closely together given the situation that we are in.  We do have an issue in terms of Mid-Central, the group which I was just talking about in that Mid-Central District Health Board provides Drinking Water Assessors services for all of Mid-Central and Whanganui District Health Boards, so we have got two District Health Boards one of which, the governance of which has no direct link with myself as a Drinking Water Assessor but the Mid-Central one does.  So it starts getting a bit complicated when you start taking the models to other regions.

- Well perhaps just leaving aside your particular situation.  Do you consider that if there is a joint governance level, that the DHB representative could adequately represent DWAs interest on it or would you be plumping for a DWA governance preference?

- I think the DWAs would feed into the District Health Board governance who employs us.  We don’t have really a separate governance group that would be transferable I don’t see.

- Do you also see a benefit given that you are the regulator and if necessary the policeman or police person, of being independent from the group.

JUSTICE STEVENS:

Or governance level?

CROSS-EXAMINATION CONTINUES:  mr gedye

- Or governance level of the group?

- I don’t think that the governance level of the group would really impact on our role as a regulator the way the system is set up at the moment.

- Well ignoring the two tier piece, what do you think the JWG, that is the working group that currently exists, what do you think it should be doing over the next six months?

- Well I still think we still have a reason to regularly meet and to make sure that we achieving the outcomes and the recommendations of the Inquiry.  Further on from that, I think there is still an area of mutual interest between all the parties of the JWG around safe drinking water particularly as far as there are responsibilities and interests in the source treatment area, particularly with Regional Council and so I think it is certainly very valuable to have ourselves, medical officer of health and District Council representatives and Regional Council representatives around the table.

JUSTICE STEVENS:

- Just part of that answer referred to source treatment level.  Do you mean the aquifer?

- Well, yeah, so one of the, and this was a discussion that I had with Horizon, which I actually haven't had with, because it was only just sort of in the last few days, when you read the NES, it talks about the granting of consents has to take into account the current treatment and certainly if you're talking wider sort of issues, sometimes having, knowing what the current treatment is and what it's doing is actually useful for the Regional Council to perform their duties as well.  But, yeah, my comment, it's not as far as the reticulation and distribution zones, which I think is a slightly separate matter.  So that’s my –

- So it is focused on enhancing drinking water assessors’ knowledge of the source?

- Well, yes.  So I can into or started working in this region with very little understanding of what the source was like.  So I've been a very steep learning curb and it has been extremely useful from that aspect.

- So just giving yourself as a random example, a new drinking water assessor arriving in the region for the first time, an obvious way of becoming familiar with the material that you are working with?

- Yeah, correct.  Yes.

CROSS-EXAMINATION CONTINUES:  mr gedye

- The section 69U of the Health Act have some relevance to this matter you're talking about.  It provides that every drinking water supplier must take reasonable steps to contribute to the protection from contamination of each source of raw water from which that drinking water supplier takes raw water?

- Yes, it does.

- And the drinking water supplier must also take reasonable steps to protect from contamination all raw water and so on.  Do you see the JWG as being a way of making that section workable?  By that I mean this is an obligation on the Hastings District Council but it's one that it would be very hard to discharge without the Regional Council’s input?

- Correct, yes.  And it certainly that in terms of our area of mutual interest between all agencies, yes, I do see it as quite a valuable perspective that the JWG can bring and if we're all sitting round the same table, not only can Hastings District Council discharge its duty under 69U, and Regional Council see well, we can have discussions around the requirements of the NES, as a regulator, I can actually see the engagement of the water supplier in that process.

- That’s what I was going to ask you.  You have an obligation don’t you to report on compliance with the DWSNZ but also more broadly with the Health Act?

- Correct, yes.

- And if you attend JWG meetings where 69U is specifically addressed with each relevant agency, then that’s a very useful forum isn't it to see how compliance is occurring?

- Yes, it is.

- Prior to August last year, how did you verify that 69U was being complied with by suppliers?

- So I can speak from my own experience in that we would go to the water supplier and ask for evidence of the work that they had gone and 69U does give some examples down there.  What work had they done to protect their sources in the last 12 months.

JUSTICE STEVENS:

- I mean another example would be 69T wouldn't it, duties where risk to water is actual or foreseeable?

- 69T, is there a Health Act handy?

CROSS-EXAMINATION CONTINUES:  mr gedye

- Well, it relates to an adequate supply.

- Yes.

- Quantity.

- My understanding –

JUSTICE STEVENS:

- Ability to maintain an adequate supply of drinking water or there may be an imminent risk for any reason.

- So it's certainly something that I have discussed with Horizons at a particular consent hearing, but it's not something we have talked about JWG at this stage.

- No, no, no, but I’m just saying that it's another example, you know, I can appreciate it's not on the agenda at the moment, but it's a reason for DWAs to remain involved?

- Oh, yeah, absolutely, yes.

- Yes.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- What do you think of the white paper process for recommendation C which relates to information sharing?

- So I think there is – it's something I haven't yet been interviewed regarding this.  The process that we went through with Horizons Regional Council, we came to the same conclusion that I think the JWG has come to here, is that actually there is a lot of information that we have that does need to be shared and that we did need a forum in agreement to address that.  So we – in the Central Region we have done that through agreement with chief executives, but as I say, it is certainly something that we have identified elsewhere.

JUSTICE STEVENS:

- Just before you move on, what's driving this initiative around Horizons and Mid-North Island here?

- So it's really come out of the Inquiry report.  So the – we’ve all read the Inquiry report, the recommendations from the Inquiry, got together and then said, “Actually, what has been recommended for this region, we should go or start a process where we are – where we have a forum that deals with the same sorts of issues.”

- So this is, in a sense, an independent initiative arising from the ongoing work that you have been involved with here and the reporting?

- Yes.

- Well, that's encouraging.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Do you agree with the comments that have been made that in order to avoid a JWG petering out, is should have specific purposes and outputs?

- Yes, I do.  I have been involved in a number of committees and technical liaison committees which have petered out and then been replaced with something else and so if there is no purpose it will die a death.

- You think it's easy or straight forward to devise a set of purposes for this JWG that would endure?

- I wouldn't like to underestimate how difficult it is going to be.  The – so for some years, I was involved with hazard substance technical liaison committees which came out of the ICI fire and that process did go on for a period of time and died a death even with that coming out of that particular catastrophic event.  The – and I think it is because the purpose was lost sight of and if we don’t have a clear purpose and understanding then I could see the same thing happening with the JWG.

JUSTICE STEVENS:

- Have you seen the draft terms of reference that are being developed?

- I am now getting a little confused as to how many different draft terms of reference there are, so I would like to abstain from that one if possible.

- Very good, well no doubt it will come to you in due course.

- Yes.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Would you expect that a joint governance group such as been described by Mr Palmer would keep breathing life into a JWG and ensure that it kept a useful life?

- I honestly don’t know.  I think the – because I don’t know how politically it would work with the tri-annual elections, I just don’t know.

- All right, can I ask you some questions about the current safety of the Havelock North water supply.  Do you consider there are enough DWAs or DWA hours in the Hawke's Bay area to ensure water safety?

- No.

- How many person hours are there in Hawke's Bay at the moment?

- Right.

- Or person days?

- Okay, so the Hawke's Bay District Health Board has got no DWAs currently on staff.

- Is Mr Malloy not?

- So he is a contractor, so he is contractor – he is actually from Nelson, he is contracted in two weeks a year – two weeks a month, is my understanding.  So he is a week on site and a week remote and I am giving what support I can from MidCentral bearing in mind that I have got all my MidCentral duties to do as well.  So I think it's – and I think there is a need for more hours and more – I think there is a need for a local DWA.

- And do your duties include measles as well as water?

- Yes, I get measles and typhoid – so, as a Health Protection Officer, I have to be on the on-call roster for health protection and do all the Health Protection Officer functions, then I have my Drinking Water Assessor functions.  I am also an Enforcement Officer under the Hazardous and New Organisms Act so I get to deal with cyanide and 1080-type issues and I am an authorised person under the Biosecurity Act so I get to deal with mosquitoes and ports of entry.

- And what do you in my spare time, Mr Wood?

- My what?

MR WILSON:

- And Myrtle Rust?

- I don’t do Myrtle Rust.

JUSTICE STEVENS:

- Right, can I just ask a question.

- Yes.

- Let's assume that the obvious conclusion that you are spread rather thin prevails.

- Yes.

- What does one do to get more resource into this area?  I mean, is it something that you elevate to DHB level?  Is it something that Dr Jones or Dr Snee can initiate?  How do we – how do you cut through all this, practically?

- Yeah, that's also an extremely difficult question.  So for a good number of years I was the only Drinking Water Assessor at MidCentral and spent years training other people up who would then get poached or trying to poach other people so that we actually had a pool of people in Mid-Central to do the work.  What would did was go through a process of scoping out the work to try and determine how many – what sort of FTE we needed to perform all the duties under the Health Act and we did that across the whole of the Central North Island, so we did it for Hawke's Bay, ourselves, Taranaki, Tairawhiti and I think it was then picked up by Regional Public Health in Wellington and Tauranga.  And so that gave us a basis for what we believed we were looking for in terms of FTE equivalent.  We then tried – so we then tried to address that through normal recruitment processes.  Now, that has proved to be extremely difficult because actually nationally I think we are very short of people who are able to be appointed as DWAs under the current system.  The other way we have attempted to address it is to get people who are drinking water operators and engineers or in the drinking water industry, train some of those people to perform quite a lot of the tasks.  We call them “drinking water technicians.”  So if we can't get someone who can be appointed, we can get someone with the experience and then try and sign off the work by someone who can be appointed under the current criteria for appointment of Statutory Officers.  So we have done quite a number of – or put a number of initiatives in place, but none of them have really addressed – I mean, practically, they just haven't worked because we are still in the same situation as we find ourselves now.  It's just – Mid-Central is in a good position at the moment and when we weren't we used to rely on Hawke's Bay, now it is quid pro quo, we are going the other way.

- But it sounds, from your answer, that it is not just a matter of money?

- No.

- It's a combination of matters that are quite complex and –

- Yes, so we have lost a lot of people to – into consultancy because actually they get paid more, but it is not solely a matter of money.  I mean, some people will make decisions because they want to work for themselves.  Money is perhaps part of it, but it certainly not the whole answer.

MR WILSON:

- So how many courses per year are run to train Drinking Water Assessors and how many spaces are on each of those courses?

- So the courses are currently run by the Opus Environmental Training Centre down in Trentham and I think really they’ll run the courses based on the number of people we can get to put up their hand and go through.  But if we can't actually appoint people to become trainees to put on the courses, then we’re a bit stuck.  So at the moment for Mid-Central is in a good place for Drinking Water Assessors because we’ve actually got three appointed which is more or less where we thought we should be, but we’re actually badly off for Health Protection Officers so which means I am on-call for Mid-Central officially two weeks in five.

- So run that past me, so the Environmental Training Centre responds to the number of available trainees, as it were –

- So they will –

- – and they will run a course only if there is sufficient trainees to fill the course?

- Well, this is – I think they’ve managed to run a course every year, but I have certainly heard some discussion backwards and forwards about how cost-effective it was if you don’t get enough people through, so.

- And what's the maximum?

- I can't – I don’t know the answer to that?

- But typically, would you get five, 10, 20, 40 through a course?

- I think we’re talking more in the realms of five or six.

- So a good scenario is we’re getting more than five per annum trained?

- Yeah.

- And we’re not convinced we have a good scenario?

- No.  And I’m not sure whether there is going to be a course next year yet because we –

- So how many in total should there be in the country?

- I can't answer that.

- But –

- We – I mean, we did our work on MidCentral area which was it – which identified about two and a half full-time equivalent people that we would need.

- Okay, so here’s a different question and I suspect I know the answer to this, is anyone doing any manpower planning or people-power planning of the need for Drinking Water Assessors at a national level?  Because if one were to assume that we need 30 and we can train five and we’ve got an average tenure of five years, we’re going backwards?

- So it's definitely done more DHB by DHB, because the DHB employs them.  I don’t – I am not aware of any national planning on – in terms of Drinking Water Assessor –

- And so obviously they retire, but you’re saying the big losses are to the consultancy field, in your experience?

- So, I am certainly aware – or to industry.  We have lost quite a lot of Drinking Water Assessors who go to Councils because they’ve got – after they’ve been working in a Drinking Water Assessment Unit and got a good understanding of Water Safety Plans, they can get poached by Councils to write all the Water Safety Plans for that Council.

- And what about the industrial sector?  Presumably some of the food manufacturing businesses find these people attractive as well?

- Yeah, I’m not aware of any that have gone that route, but it wouldn't surprise me.

JUSTICE STEVENS:

- Who does this sort of personnel planning career management in the Drinking Water Assessor space?  Is it the DHB initiative or is it the Drinking Water Assessors?

- No, it's generally the DHB sort of initiative, so the DHB has got the Human Resources Department, they do the advertising and new appointments, that’s where the – we have our coordinators or team leaders set in DHB, they have our professional advisors in DHB.

- It probably needs some more information on this in due course.

MS RIDDER:

Sure Sir.

Mr Gedye:

Mr Roberts has given me a good figure from the wit – the jury box, Sir.  Between 2004 and 2016, which would be – can't do the arithmetic – 63 people have qualified.  So that’s 12 years.

MR WILSON:

Five a year.

MR GEDYE:

Five years but I imagine Water New Zealand could give us more information and data as well as probably Ms Ridder’s clients.

JUSTICE STEVENS ADDRESSES MS RIDDER AND MR ROBERTS:

Yes that is what I was thinking, that would be really helpful Mr Roberts because you know, we may be asked to make some recommendations.  What has struck me significantly was that answer that Mr Wood gave that it is not just a matter of money, so one really needs to understand the dynamics and what the drivers are and why, if there is a need or first of all is there a need, is there a perceived need at DHB level, if so what that level is the need and what are they doing about meeting that need.  All of those important questions because unless we understand those aspects we are not well placed to make recommendations.

MS RIDDER:

No I understand that Sir.

JUSTICE STEVENS:

And importantly if the DHBs would like us to make some recommendations, then what are they.  And are they realistic because we do not want to be making recommendations that are –

MS RIDDER:

That create other problems Sir.

JUSTICE STEVENS:

That create other problems or are unrealistic.

MS RIDDER:

Sure, no that is all good.  Is there something you would like to hear from perhaps Dr Jones when he is in the witness box tomorrow, he might be closer to the issue than Mr Woods.

JUSTICE STEVENS:

Quite possibly.  Well I mean it is interesting that we have had Mr Woods’ perspective and to the extent that Dr Jones can contribute in a preliminary way that is good but you may well need some more time to explore this and by all means talk to Mr Roberts as well.

MS RIDDER:

Look I know the issue is top of mind for the DHB in terms of DWA resourcing, it is struggling with that issue at the moment as Mr Woods has said.  So there will be some top of mind stuff that I presume Dr Jones will be able to tell you but otherwise we can feed information through Mr Gedye to assist.

MR WILSON ADDRESSES JUSTICE STEVENS: NATIONAL ISSUE

JUSTICE STEVENS ADDRESSES MR GEDYE AND COUNSEL:

Well Mr Wilson rightly raises the question of the Ministry, what planning is being done there and is there information that can be fed.

MR GEDYE:

We will be asking all agencies Sir.  I was going to say we need to speak with Ms Arapere and Ms Butler about the Ministry of Health because they actually approve DWAs and have a very big role.  In addition Opus Training has filed an address for service and wants to make a submission so we should be talking to them as well.  All relevant agencies will be asked to contribute and people like Mr Rabbits can no doubt add a perspective as well.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Mr Wood, do you see merit in DWAs having water operator experience or background?

- So I think there is a number of different issues that DWA has to wrestle with under the current legislation.  So obviously at the moment DWAs are health protection officers so they come from an environmental health background which does have a value in terms of some of the things that we were working through, particularly with the Hawke’s Bay outbreak and because there was a definite health link.  There is also a water science type link so my background is actually not from health, I had to be retrained in health to do what I do but my original background is as a chemistry degree, so I am a water chemist.  That is where I started so then I bring a chemistry expertise to it.  But I am not a microbiologist for example so I was listening with quite a lot of interest to Dr Deere because some of the issues which I would identify as a water chemist, are not necessarily exactly the same as you would a water microbiologist and that actually led to some of my comments on the WSP which I am sure we will get to.  The other part of that is yes, operations and engineers and further part of that is economics because some of these things have economic type aspects and I was talking to Mr Rabbits about this at lunch time, so it is certainly an issue where we actually, at the moment have one person who is a DWA who gets to look at whether a Council or water supplier is taking all practicable steps to meet the Drinking Water Standards which includes in the Act an economic aspect which if a Council or a water suppliers says that is not economic, I wouldn’t have the expertise to address that at all.

- Well accepting that there are many disciplines that have some relevance, is not the experience of a water operator or a network operator of some of the greatest relevance to the work that the DWAs do in considering Water Safety Plans and compliance?

So yes it is and that is part of the reason that we went down the route of trying to employ operators and engineers as drinking water technicians.  We did identify that that was a weakness within our own organisations.

What is the reason why those persons couldn’t be employed as a drinking water operator?  Does it lie with the Ministry of Health?

So we can employ them but at the moment, the criteria for appointment as a statutory officer requires that a drinking water assessor be a health protection officer.  That is in the criteria.

The Ministry of Health won’t approve a person who is a water operator?

They won’t appoint.  Now we can still employ them and get them IANZ accredited and get them doing quite a lot of the work.  It just means that we then have an administration function where someone who is appointed, has to sign off that work.

MR WILSON:

But that is a job description issue internally within the DHB is it not?

Yes and as I say we have actually had, or we currently have two people who are appointed into those roles within the wider region shall we say.

But they have been appointed as – I think you call them?

We have called them drinking water technicians.

But they have the DWA qualification?

Yes.

CROSS-EXAMINATION CONTINUES:  mr gedye

They do the course?

They do the Drinking Water Assessor yes.  So sometimes that just means adding six more modules to the course that they have already done to then do Drinking Water Assessor work, so they still have to be IANZ accredited, so they still go through the IANZ process.

DR POUTASI:

To the best of your knowledge has the Ministry given any consideration to not requiring the health protection officer qualification?

I can’t answer that I am sorry.

MR WILSON:

Well that was going to be my question.  Do you know whether that guidance is coming through at the DHB level or at the Ministry level?

So the criteria for appointment as a statutory officer is a Ministry document.

And so the Ministry is insisting – and correct me if I am wrong, that statutory officers be both health protection officers and drinking water assessors if they wish to be drinking water assessors?

The current, my recollection is that the current criteria for appointment for statutory officer, for a drinking water assessor says that a drinking water assessor must be a health protection officer.

And that is a requirement from the Ministry?

Yes.

JUSTICE STEVENS:

Statutory I think is what you are saying.

Yes.

CROSS-EXAMINATION CONTINUES:  mr gedye

Well section 69 Z and K doesn’t have that requirement does it?

No, it is not in the –

Generic only.

– if the – so I think it’s in one of the documents that I have been looking through, many folders. The criteria for appointment of statutory officer is a Ministry document that is given to District Health Boards.

- I'd invited my learned friends behind me to assist with all of this material in due course for the submission.

MS ARAPERE:

Your Honour, if it would assist, we did file that criteria document in stage 1 with Ms Sally Gilbert’s brief of evidence and we can find the document number and –

JUSTICE STEVENS TO MS ARAPERE:

- That would be good.  I mean all this needs to be pulled together and you know, what we are trying to come up with is a set of recommendations that are practical, that are reasonable and that are implementable, so it would be really helpful to understand if the Ministry want to maintain that requirement, why and if it could be dispensed with so that the technicians could become drinking water assessors or it might make the prospect of employing people easier.  Those are all things that need to be looked at.

- Yes, Sir.  We'll take instructions on that.  The criteria which have just been handed to Mr Gedye are CB157 from stage 1 in the common bundle.  Thank you, Sir.

- That is most helpful.

- That’s clear and I've added that to the list of things that I'm going back to the Ministry on.  Thank you.

- That is great.  Thank you.  And the message to get across is that we want to be results-focused.

- Absolutely, Sir.  That’s understood.  Thank you.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Yes, thank you for that, Ms Arapere.  We did of course have that material.  I guess I was referring more to where are we today and how should it be.  Mr Wood, in your opinion, how many drinking water assessors should the Hawkes Bay District have today?

- My, from the work that we did, my recollection is that it is about two and a half FTE that we calculated out.  Now, I can go back and check that with –

- No, that’s useful.

MR WILSON:

- But that is a very – by FTE you mean full-time equivalent working on drinking water assessment work?

- Correct, yes.

- So if you were to assume that they had half of their role on health protection work, you are talking about five bodies on the ground?

- Now, I'd need to, that work that we did was based around people maintaining their competency as a health protection officer as well because that was a requirement as a statutory officer.  So some of that health protection officer time is built in.  So –

- But it is more than two and a half people on the ground?

- It is more than two and a half people on the ground, yes, but it's probably not as high as say five.

CROSS-EXAMINATION CONTINUES:  mr gedye

- An anecdotally you'll be aware there were 10 transgressions in the two months between mid-February and mid-April?

- Yeah.

- Places like Esk and so on.  How did the DWAs cope with that?

- So we called heavily on Matt Malloy to be available in terms of the work that he was doing.  So he was I think on site for a couple of those and I have been involved remotely in reviewing reports and teleconferencing into operational meetings and turning up to operational meetings when I can as well.

- Plus the JWG when you've got nothing else to do?

- Yes.  So I'm over at least one day a week at the moment.

- And then Napier’s had a number of transgressions hasn’t it?

- Yes, correct.

- Have they added load to the sparse resource in this region?

- Yes.

- What scope is there for private enterprise to carry out some of the functions of the DWA and is Mr Molloy a private contractor?

- Mr Molloy is a private contractor, yes.

- So what's to stop a system where all sorts of water experts contract their services to DHBs to boost resources?

- Well, that’s where it starts, you would have to talk to the DHB in terms of financial cost and risk and those sorts of things.  So I can't specifically answer that.  It's, part of it is also around appointing those people to be drinking water assessors.  So Mr Molloy was previously a health protection officer and has that skill set as well.  So he's appointed as a health protection officer and a drinking water assessor under the accreditation that we hold in terms of our partnership.

- From your point of view, would it be desirable to separate out health protection duties from DWA duties?

- Well, the variety has been one of the things that’s kept me going but I have to say having been at the Inquiry now over stage 1 and stage 2, that actually I could have done without the measles and the typhoid, so, yes.

- Well, if you leave aside job satisfaction, as a systems matter, is it not better to have dedicated DWAs who have that as their only job?

- I think as a systems yes, it is.

- There's enough work and enough responsibility isn't there to justify a full-time role?

- Yes, absolutely there is, yes.

JUSTICE STEVENS:

- And it might help recruiting?

- Yes.

CROSS-EXAMINATION CONTINUES:  mr gedye

- How many people are there like Mr Molloy around New Zealand who are private contractors who could fulfil this role?

- I don’t know I'm afraid.

JUSTICE STEVENS:

- Just while we are in this point, the drinking water assessor group seems to be a very flat level group in the sense that you all operate within your different areas, geographic areas.

- Yeah.

- You do not report to a chief drinking water assessor?

- No, correct.

- And you are not managed by any other drinking water assessor?

- Correct, yes.  So –

- Is that a problem?

- It can create difficulties from time to time so sometimes when I'm reporting through to my DHB manager, I have to go back and explain things that really I wouldn't necessarily have to explain if it was someone who was really intimately familiar with what I do and my DHB manager is actually really very good because he has been in the role for quite some time, so he's got a better understanding of what I do than lots of other DHB managers.  So it's certainly, it does have its complexities.

- And the other aspect of it, just through the evidence that you have brought to the Inquiry, and for which we are very grateful, suggests that, you know, within the drinking water assessors, there are going to be those with different abilities and different skill sets and different, I suppose, responses to different problems and sometimes it is quite good to have a mentor?

- Yes.

- And I perceive for myself that you have been fulfilling that role but there is no recognition for that or –

- No, there isn't but it is certainly when – so we set up the Central North Island drinking water assessment unit really in response to the fact that we felt as drinking water assessors a sense of professional isolation and that we didn’t have a mentor and we didn’t have the networks and so that was one of the reasons for coming together in the partnership that we have, that we have now with, from our Central North Island drinking water assessment unit is now rather misnamed because we cover from Tauranga to New Plymouth and down to greater Wellington and we have set up roles within that so that we can provide some sort of expertise and have different people who are doing some of that mentoring-type role.  So our drinking water technician, who is a operator engineer in Taranaki, has got a – we've given him a training role because actually we think that’s important across the region and I've had a technical manager-type role, technical manager operations to try and provide some of that mentoring across what is now a lot of the North Island.  The same issue was identified down in the South Island and a South Island drinking water assessment unit was set up covering the whole of the South Island to try and overcome some of the difficulties that you have alluded to.

- It may be that this would helpfully be put forward as a if you have got some suggestions for Stage 2 that you would like to see us consider because what one – what might be looking for is a career path?

- Yes, I understand.

- And opportunities for leadership, opportunities for mentoring and generally making the job more satisfying.

- Yeah.

- So that you keep DWAs in the job longer.

- Sounds good to me.

MR WILSON:

- Mr Wood, how easy would it be to take the historic work that you did that I understand was in an area roughly equivalent to what your so-called central unit is now covering and extrapolate it up to get a national picture, if you like, of what an ideal resource might look like?

- So if that would - it would be certainly possible to do that.  The way we set it up was based around the number of suppliers of different size that each area had.  There is no reason why we couldn't extract information from the Register of Drinking Water Suppliers and do – run that model for the country.  It would be sort of – would could do that, it's –

- Could be possible to do it and include it in a submission before the August hearings?

- I would need to make sure that we still have everything that we need to be able to run it.  I could give you – or I could give Ms Ridder an indication of what we should – whether we could do it or not, but yes, I was certainly done for us in the situation that we found ourselves in two or three years ago, four years go.  Yeah, but I still valuable, I think, yeah.

JUSTICE STEVENS:

- The reason – oh, it would be valuable and the reason we’re interested in this is that we want to – this is a one-off opportunity for you to contribute to a better system.

- Yep, absolutely understand that.

- If this would make the system better.

- Yep, so at best, I am certainly quite prepared to go back and make sure that we have got the model and try running the model over the information that we have got for the country and provide that through to counsel – our counsel.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Mr Wood, the Stage 1 report included an observation that the DWAs had been lenient or had adhered to the cajoling and encouraging school of thought.  What's your thoughts on whether the DWAs should nowadays be more ready to wave the stick and to escalate matters and to act as enforcers when necessary?

- So certainly separate to this Inquiry and even before the Havelock North incident occurred, we identified a need to be more forthright, if that is the right word.  That is part of what our escalation policy was an initial attempt to address.  We’ve certainly taken a – from the MidCentral perspective, we have taken a different perspective in terms of implementation and to that end we poached another DWA with a different skill set from down south so that we could actually do more of the good cop/bad cop-type stuff, so we’d have somebody who was able to go in there and wave the big stick.  You know, another pair of eyes that we could call on.  So we’re certainly quite conscious of the fact that this – the legislation is there and that there’s no point in having legislation there if it is not going to be used for anything.

- This feeds back into what His Honour was asking about, who actually evolves and considers changes of policies or methods of operation if you don’t have a conventional management structure?  Is what you’re talking about discussions you’ve held within Mid-Central?

- We’re – and the Central North Island – we’re trying to, yeah, we’re trying to evolve that ourselves from the bottom up rather than from the top down.

- Well, we talk about the Hawke's Bay, who is there to oversee the policy and operations of the DWAs in this region?  Is it in effect the DHB or –

- No, it's – the DHB has the employment arrangement, but we are in that position of having the statutory accountability under the Health Act to the Director General.  So there is two parts to that.  There is the Ministry of Health part and there is the DHB part.

- Well, in the past when you were pursuing the cajoling method, was that at the direction of the Ministry of Health?

- It was encouraged by the Ministry of Health.  So the Ministry of Health has – and again it's in the criteria for appointments of Statutory Officer – a pyramid-type diagram which certainly looks at the bottom tier of that pyramid as the cajoling-type approach and the very top of that pyramid is the legal action-type approach and there’s two steps, I think, in-between.  So whether it's – it's certainly a discussion that we have in terms of – with the Ministry of Health as to where on that pyramid things are currently at, if that makes sense.

- Well, following the Stage 1 report which said that the DWAs were too soft, has the Ministry been in dialogue with you saying perhaps you should be less soft?

- Not directly with me, no.

JUSTICE STEVENS:

- So what's happened to our report and the discussion about – the comments in there about the role of the Drinking Water Assessors?

- Well, certainly the Drinking Water Assessors have taken it on board, but I think we are still trying to drive it ourselves rather than having direction.

- All of which suggests that this flat line model of –

- Yeah, I understand exactly what you are saying.

- Yes, I mean, who –

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Do you produce a monthly report to anyone or?

- Yes, I do.  I report through to MidCentral District Health Board based on the template that they give me, so.  So that goes – my report, my monthly report, goes to co-ordinator and then to a service manager and then to – actually, I don’t know where it goes after that, mhm.

- Would you find it preferable to report to one employer or one master?

- Yes, I would.

- Is the direct line to and from the Ministry of Health an effective one, from your point of view, and a beneficial one?

- At the moment it is, I would say, rather ad hoc, so every time an issue comes up that I feel needs to go to the Ministry, I will phone them up or email them.

JUSTICE STEVENS:

- Just while Mr Gedye is looking for his next question, the faults and failures of the DWAs starts at paragraph 418 and goes through to 481.

- Yeah.

- And I am sure you have read every word of it.

- I have, yes.

- And as I said earlier, this report is, in a sense, sets the framework for Part 2 and is to provide context to the work – ongoing work and are you telling us that you haven't heard from anyone about how to deal with this?

- I haven't heard from the Ministry about what the approach will be.  I mean, we’ve had internal discussions, but –

- Between DWAs?

- Between DWAs and with our own DHB management.

- Yes.

- But I haven't had dialogue with the Ministry.

MR WILSON:

- And who initiated those discussions?

- We did, the DWAs did.

JUSTICE STEVENS:

- I mean, there is some pretty big meat in there that needs to be looked at because we are now moving on to systemic issues that flow out of this context.

- Yep.

- Improvements for the future, how one might change and recommendations as to the regulatory system, all of which we have got to have completed by the 8th of December, so it just seems to me that there is not much being done.

- I can't speak for every agency but certainly we, there are a couple of things that we are trying to do in terms of getting DWAs together to make a submission, you know, with somebody like the PSA on our behalf and there are a number of DHBs who are certainly looking at progressing it.

- Well, that is helpful.

- It's not being ignored.

- Is Ms Ridder available to help you on that?

- Yes, Ms Ridder’s been very helpful with, we've had, we've started that dialogue in terms of where to from here.

- All right.  Well, I do not want to pre-empt any work that is going on and we do not need to necessarily know about it but it is important that we have material by the deadline.  I think it is the 21st of July and to the extent that we want to contribute to the designing of a better system, we would love to hear from you or any of your colleagues.

- Yeah.

- Or from your DHB boss and hopefully the Ministry of Health.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Just finally from me anyway, Mr Wood, on the local current situation, am I right that physically in Hawkes Bay area we have Mr Molloy for one week a month?

- Correct.

- And he's available –

DR POUTASI:

- Sorry, could I interrupt there?  I understood two.

- So one week on site and one week remote.

CROSS-EXAMINATION CONTINUES:  mr gedye

- So the other week he's in Nelson?

- Yeah, if he ever gets home.

- And for the one week a month Mr Molloy is in this region, does that extend from where?  Dannevirke to Wairoa, something like that?

- So the region doesn’t cover Dannevirke.  We cover Dannevirke from mid-central.  That is four Councils.  Central Hawkes Bay, Hastings District, Napier City and Wairoa District.  So it's Wairoa through Waipukurau.

- And for the one week a month he's here, is he also doing measles as well as water?

- No.  We have got Mr Molloy dedicated to water.

- He's water only?

- Yeah.

- So if there's a major transgression or even, God forbid, an outbreak in the three weeks a month he's not here, what happens?

- Well, a lot of them end up coming through to myself on the phone or we're dealing with it remotely at the moment.

- How does your DHB feel about so much of your resource being given to another DHB’s area?

- I think it certainly my manager has not raised any issues with it at this stage but at some point, it's not sustainable.

- It's not something you could do forever is it?

- No, absolutely not.

JUSTICE STEVENS:

- Sounds like he is being, if it is a he, is being very gracious and very patient and very fore-bearing.

- Yes.

MR WILSON:

- Otherwise from what Mr Wood said before, there is a bit of quid pro quo has gone over on to parts of history as well.

- Correct, yes.  So there are and we also are aware that if the Hawkes Bay District Health Board falls over in terms of being able to perform its drinking water assessor work, that affects the accreditation for the entire Central North Island.  So there are reasons why we want to support.

JUSTICE STEVENS:

- But it is not really satisfactory is it?

- No, definitely not, no.

- So let us not mince our words.

- It's not sustainable long-term.  It's at best a band aid.

- A what?

- Band aid.

- Band aid, thank you.

mr gedye

Now, Your Honour, I wonder if we should take a break because there's some issues about how many other topics I cover with Mr Wood versus how much time we've got left.

JUSTICE STEVENS:

And there may be things going on that we are not aware of and I do not want to be unreasonable or appear to be unduly critical if we are going to hear from others involved later on.  So by all means, talk to Ms Arapere and maybe if we can be assured that these matters are going to be addressed and will be rightly considered in August and beyond then, probably we can let Mr Wood go back to Palmerston.

MS ARAPERE:

Yes, Sir.  Thank you.  We had understood that this, particularly under issue 12, would be dealt with in the August hearing week.  I can assure the Panel that the Ministry of Health takes the stage 1 report very seriously and there are multiple work-streams underway in the Ministry.  However, what we had focused on for this hearing week was just issues 1 and 2.

JUSTICE STEVENS TO MS ARAPERE:

- And rightly so and you are quite right to remind us to stay within issues 1 and 2.

- Well, it's your courtroom, Sir, but I did want to reassure you that there are multiple work-streams underway in the Ministry to prepare for the 21st of July filing date.

- That is helpful and I guess it is just the fact of having the witness here and to the extent that we can encourage, cajole and arouse interest in a focused and productive outcome that will allow us to make some good recommendations.

- Absolutely, Sir, and that is understood by the Ministry.  Thank you.

- Wonderful.  Well, we will take a break for 15 minutes and then hopefully we can let Mr Wood go.

MR GEDYE:

Yes, I just want to discuss whether the water safety plan and a few other issues, whether the Panel wants to hear from him or whether there's no need for that so we could discuss that and just to be fair to my friend, she makes a very good point.

JUSTICE STEVENS TO MR GEDYE:

- I agree.

- I think the problem is I wanted to address today’s problems but in so doing, it raises immediately the structure and the system but as long as we've covered today’s problems in the area, that’s all I hope to achieve today.

- And as long as the work is being done and we do not get to August and find that we do not have the tools to deal with it.

- It's been very interesting and useful I think but the real discussion is going to be in August, not now.

- I agree.

- Thank you, Your Honour.

- We will take 15 minutes and be back at quarter past.

INQUIRY ADJOURNS:		3.57 pm

INQUIRY RESUMES:		4.13 PM

WITNESS ON FORMER AFFIRMATION

CROSS-EXAMINATION CONTINUES:  MR GEDYE

- Mr Wood are you familiar with section 69 ZZZ of the Health Act?

- Yes, I am.

- I wonder if you would be kind enough to answer a question from Mr Wilson about that section.

QUESTION FROM THE PANEL: MR WILSON

- Mr Wood I was curious to know what, if anything, is done in terms of the annual assessments for compliance with the Drinking Water Standards in terms of assessing a water suppliers satisfying of that criteria, in other words ensuring backflow?

- So I find – it is interesting you ask this question – because section 69 ZZZ is my least favourite section of the Act on the basis that section 1 has an “if” statement and section 2 then has a “may” statement followed by an “if” statement and by the time you get through an “if” “may” “if” it is trying to nail jelly to a wall I am afraid.

- Having said that, you understand the importance of backflow?

- Absolutely.  And so I have to admit that I put the section of the Act to one side and then I go to – it is something that I regularly go to my local authorities to ask, what is your policy on backflow?  What is your commitment, can you show me your test reports, can you show me your IQP test reports on the backflow prevention devices that you have.  It is something that I specifically look for in terms of water safety planning and there is something that I always ask on a water supplier, when it comes to Water Safety Plan implementation but I do tend to put the Act aside because I really don’t like the section.

- But quite specifically, in terms of the Annual Report that the Ministry produces, is backflow one of the criteria that is or is not satisfied?

- So the Ministry asks us to report on a series of sections, I can’t remember specifically – there is four or five sections that they ask us for but it does not cover, but they do not ask about section 69 ZZZ.

- Thank you.

questions arising -   all COUNSEL – NIL

JUSTICE STEVENS ADDRESSES COUNSEL:

Just before Mr Wood leaves, the Panel is troubled by the matter of staffing, the current matter of staffing of Drinking Water Assessors in the Hawke’s Bay area.  We consider that to be a matter of immediate concern regarding the safety of the drinking water in Havelock North and Hastings.  The concerns have arisen from Mr Wood’s evidence and I am sure you will appreciate why.

MS RIDDER:

Yes Sir.

JUSTICE STEVENS:

It may be something that Dr Jones can help with tomorrow when he gives evidence and it may be that something that has under control, it may be something in respect of which he is in discussions with the Ministry but between the DHB and the Ministry, we would expect the matter to be addressed as a matter of urgency.  Because it is quite frankly intolerable to have one week per month of a temporary DWA and an availability remotely for another week, to be covering the work of two and half FTEs.

MS RIDDER:

Sure, Sir.

JUSTICE STEVENS:

It is no criticism of you at all.

MS RIDDER:

I am not taking it as criticism Sir.

JUSTICE STEVENS:

But we are really worried about it.

MS RIDDER:

We will be able to update you – we will be able to update Mr Gedy on the current situation what the DHB has been doing about it overnight and Dr Jones will be able to talk to that in the witness box tomorrow.  But as my learned friend  Ms Arapere said, this was a matter that we had thought of for August, but of course, we understand that yes, the relevance to the current situation and the safety of the Havelock North drinking water.

JUSTICE STEVENS:

And if you extrapolate this immediate concern out across the country, which may or may not be proper, but it is certainly open to that view, then it maybe that the situation is quite serious.

MS RIDDER:

Yes Sir it may be.

JUSTICE STEVENS:

Now I will just ask my colleagues.  Did you have anything you wanted to add?

DR POUTASI:

No I think what we are concerned about is the immediate and that brings it into the view of what we are doing now, in the sense of immediate concern and then yes, of relevance obviously to the August Inquiry but it would be really good to hear what is in place to be able to mitigate the effect of resource, yes absolute resource shortage and the impact on the DWAs who are endeavouring to support the situation.

MS RIDDER:

No that is no problem.  That will be undertaken overnight.

JUSTICE STEVENS:

That would be great.  And you will have appreciated, we understand your reservations and we take on board totally the points you made before the break, but we have decided as a Panel that it is relevant to safety.

MS ARAPERE:

I understand that Sir and I will take instructions.

JUSTICE STEVENS:

- Thank you.  Mr Wood, you are now free to go.  Thank you for your attendance and thank you for the material and if  in your response to the Stage 1 report you need any further assistance, then – and it's not being provided – then you should let counsel assisting know because it troubled all of us to hear you referring to having to seek help from the Union.

- Okay.

- All right?

- Yes.

- Thank you.

WITNESS EXCUSED

Mr gedye re-calls

dr deere (on former oath)

justice stevens ADDRESSES dr deere – spell out new acronyms

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- I want to ask you about TCs.

- Yes.

- Total coliforms.  Now, I understand that of the two litre sampling, 4.1% of the samples produced a total Coliform result, is that your understanding as well?

- I have not checked the figures, but I have no reason to doubt that.  I’ve not done the maths and checked that, but no reason to doubt that.

- Without descending too much into precise statistics and numbers, am I right that there has been a significant total Coliform result from sampling in recent months across all of HDCs bores?

- There has and we’d expect that for most what you might call normal water.  Very well aged groundwater may be low in total coliforms, but normal everyday water you’d find in any puddle or in a stream or anywhere, water that falls into the – a rainwater tank, that would have total coliforms in and so total coliforms are used in the US in particular as part of a simple indicator for the presence of fresh material in groundwater to show that it is not well-aged groundwater.

- And is that the real significance of TCs that you are not withdrawing pristine aged secure water?

- That’s how they’re used, yes.  So they’re not a perfect indicator, but you don’t usually find total coliforms in well-aged groundwater.

- Does the total Coliform result over the last several months suggest to you that it would be wrong to treat the Hastings bores as secure?

- They certainly have a total Coliform level that would form difficulty with the American standard that has a total Coliform test as part of their groundwater rule and given how old the water ought to be if those models are correct, you wouldn't expect to see total coliforms.  So the implication is there is some fresh ingress into some of those bores at some period.

JUSTICE STEVENS:

- And that is supported by the water aging work that has been done?

- More recent work, yeah.  The old – there was some of the work we saw figures of 30-40 years and you wouldn’t see total coliforms in deep artesian groundwater of that age, so that suggested that wasn’t consistent with those results, earlier results.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- I want to ask you briefly about the FAC data.  Have you had available to you the spreadsheet of FAC test results?

- I got a spreadsheet on Monday, but I haven't gone through it yet, so I can't – I have to confess I haven't gone through that data yet.

- Can I just put a couple of propositions to you then.  If there were 5165 samples in that spreadsheet, if nine – 1.9% had an FAC value of less than .2, would that cause you concern?

- If that were the water coming out of the bore post-treatment it would.  If it was the water in the customer taps, that wouldn't be surprising. We often see difficulty getting FAC above 0.2 milligrams per litre in dead-ends or areas of low turnover.  A few days is enough to lose that chlorine.  That wouldn't be surprising and we, in the industry, recognise that as a weakness in our multi-barrier system that we usually have low chlorine in those systems.  I recently saw a paper by the Victorian Government Regulator on their results and they showed that most of their E.coli transgressions were linked to what they thought was contamination of the distribution system and many of those were linked to that sort of level below .2 chlorine and they made the point, “We’d like to see better chlorine performance,” but that kind of percentage, a couple of percent below .2, would not be uncommon in the distribution system.  That would be very – it would not be a good result just post the treatment plant, so I’m not sure where their samples were.

- But even at the end, isn't dead-ends and the outer reaches of the reticulation, isn't the supplier supposed to maintain a minimum of .2?

- That’s the goal and it's one of those things that if you built a new system, the systems often get built to avoid dead-ends, so they build them – even if there is a dead-end street, they make the water pipe continue through –

- Yes.

- – or they use narrowing pipes with a smaller bowl, with a smaller pipe at the end, to keep the turnover of water, but many older systems just weren't built like that, so we’re inheriting a lot of systems where it's very difficult to practically achieve 0.2 at the end, but not have excessive levels at the start, and so it is common to have poor performance on residual chlorine and so it can cause slimes and biofilms and odours and other problems to arise.  It is a problem.  It is an industry problem.

- With a well-run system, should the FAC results be relatively stable?

- They would if the system was – had automated dosing systems which is where Council is moved for – which is what Council is moving to with automatic feedback control with continuous chlorine analysers and then some active management of that chlorine to respond to changes in water demand, different times of year, different seasons, then it would have.  The difficulty for Council is that because the chlorine is being introduced for the first time, all those sort of ancient chemical and biological features that would react with chlorine, as those reactions occur and it becomes stable, in the interim it is hard, it is hard to manage that chlorine.  It will take some time, possibly some years, to learn the system well enough to get the dosing balance right.

MR WILSON:

- So Dr Deere how long would you anticipate it would take to – for the chlorine to oxidise the organics that are in a system?

- The – there’s an instantaneous reaction, but the difficulty is the biofilms and the chemical sort of chemical films in the pipes.  They can take quite a long time to gradually oxidise and work and change and they can slough off, you can get metals being released and so-on from that effect.  Slimes can slough off and so-on.  So it can take – it could take some months to get a – possibly even toward the year 'til you get a stable system and then the Council needs to start to learn at different times of year, so when it's warmer the chlorine breaks down faster, in holiday season some areas have higher demand than others, so it will take some time to learn the system and get a high performance on free chlorine residual at the end of the system.

- And so what you are telling me is that as soon as you have introduced chlorine into a system such as this bore, that has not historically been chlorinated, you will after a relatively short period be able to detect free available chlorine at the ends of the system but that that will not be stable because it will take quite a while for all of those processes you have just described to –

- To form a sort of new equilibrium.  That’s why it takes some time, yes.

- So there is a difference between measuring free available chlorine at the end of the network post-introduction and getting to a stable environment?

- Correct, and also what operators tend to do is they learn over time either by having spreadsheets and referring to those from previous years or just by learning from just gut experience, how high to set the chlorine and re-chlorination where they need to re-chlorinate, what time of year they need to re-chlorinate, whether it's dosing with tablets into a water tank or having a proper dosing, system of doses liquid or gas chlorine and it takes time to get that.  It's a lot of work to do that.  It's not an easy job.

- On a network the size of the combined Hastings/Havelock network, would you anticipate the need for permanent re-chlorination stations?

- I don’t know what the chlorine demand is of the water.  I would hope that the groundwater would have a low enough chlorine demand that they would not have to have excessive or any re-chlorination but if they have areas that have long residence times in the system of days, maybe large water tanks or large pipes serving small populations, they may still need to re-chlorinate but the chlorine demand in this water should be very low.  So it shouldn't be as big a challenge that would be from a river water for example.

- And tell me, because of all these complex processes are going on where bio-films and presumably some of the coatings on the inside of some of the fittings will be oxidisable as well?

- Correct.

- How many of the taste and odour complaints that will have been experienced when chlorine was first introduced are due to pure chlorine and how many are due to the complex chloro-organic compounds that you will have in this transition period?

- Yeah, the guidelines that are available that relate to taste and odour in water generally say that pure free chlorine in pure water doesn’t have much of a smell and you wouldn't tend to notice it.  It's normally the bi-products that are what you notice.  So I suspect the kind of levels that Councils been dosing aren't terribly high.  I suspect the problems are more to do with the bi-products rather than the pure chlorine itself.  It's not always the case but –

- And that is certainly my experience and so the point I suspect that I am asking of you is, apart from the fact that the community will get used to it, in fact the odour-generating compounds will dissipate with time and therefore the community objection to chlorine, in fact there will be nothing to detect and therefore they will not have an objection from a taste or a smell point of view.  They may have a philosophical objection but that is a different matter entirely.  You would anticipate that the actual ability to detect an odour or a taste in a chlorine to dissipate with time?

- Absolutely.  In fact I was surprised when I first visited in April, I went and watched one of these chlorine-free taps 'cos I thought nobody will be bothering with this and there was queues of vehicles, literally queues of people getting the water and I found that surprising because groundwaters generally don’t create much of taste or odour problem when you mix them with chlorine and Council advised that they have had some problems at the first but those problems are dissipating.  The water is getting easier to chlorinate because the network’s stabilising and they're also looking at, they're moving to automated chlorination systems that will have a much more reliable and stable chlorine level.  The current systems are temporary and they're not, it's difficult to chlorinate with the current systems.  So I think you're right.  I think the chlorine-related taste and odours will disappear and be left with largely the kind of placebo effect, the kind of false, people thinking it's chlorine but they probably can't smell it or taste it.  So I think you're right.  The system should be able to be chlorinated in a way that’s acceptable with relative ease once the automated systems are put in.

- But are you concerned at the current levels of .6 or so that have been reported as the average?

- .6 is about textbook for what you try to achieve at customers, it's just below the normal area people can smell or taste the free chlorine in and of its own right and then it's a good stable, a good effective residual.  So that’s a – the numbers that they are achieving are appropriate numbers to target at this point, yes.  In fact we don’t recognise a health concern until we get to about five milligrams per litre but we recognise taste and odour concerns around one milligram people can start to smell it at that sort of level.

- And just while we are on this matter, the Hastings evidence reports an acceleration of problems with pin-holing service in copper service pipes.  Have you experienced that before with the introduction of chlorine?  That has been attributed to a bio-film being sloughed off and exposing existing pinholes.  Is that –

- I've experienced extensive problems with corrosion where there hasn’t been chlorine, where the bio-films create pinhole corrosion and other forms of corrosion and chlorine is often used to try to help reduce the risk from those bio-films.  Council’s advised that, have they told you that they think possibly this increase is just a re-stabilisation where these relatively stable bio-chemical films are then disrupted causing pinhole corrosion but that should be a short-term thing.  In the longer term, chlorine actually tends to give you a more stable pipe network because you inhibit the biological activity that creates this acidic effect that causes metal corrosion.  So I think although it may cause short-term problems, my advice was, to Council was in the long-term, you'll be better off with chlorine.  You'll get less corrosion rather than more in the long-term.

- And less blue staining of your sanitary wear?

- Correct, and there may be, they’ve been telling me they’ve had some issues with some, it appeared to be metallic colours, that bluish sort of colours from perhaps copper leaching again as the system re-stabilises but once again, chlorine generally gives you lower risk of pipe leaching rather than more.  So again, once it stabilises, they’ll be better off but there's a, it's that hump you’ve got to get over but the advice I've had from Council this week is that things are getting better now, that it's moving in a good direction.

JUSTICE STEVENS:

- Just before you go on, I wanted to ask, Dr Deere, we have heard reference to recommendation E to the joint working group.  That is the one that talks about investigating whether the Havelock North reticulation and distribution systems are fragile or vulnerable and whether they need maintenance repair work or improvements in order to deliver safe drinking water and the discussion that we were having earlier, and I am sure you heard, was that that is really a task that lies with the water supplier.

- Yes.

- So there is the possibility that that recommendation be varied to be directed, works that the District Council would undertake itself.

- Yes.

- Have you been instructed in that area, in other words, your brief would include that scope?

- Yes, correct.  So when we talked about doing the water safety plan, what I've been asked to do is make sure that the water safety plan improvements cover the inspection, the maintenance of the barriers in the distribution system that protect water quality.  So that includes the roofing and protective structures on the reservoir, storage reservoirs, managing the pressure to make sure we don’t get water sucking into the system, that it stays pressurised.  That includes the materials that are used, the way that those burst pipes and things are repaired and also the discussions that you have with the DHB about the backflow prevention because there are still some sites that don’t have what we would consider an appropriate level of backflow prevention.  They are less urgent than the matters from the bore but nonetheless they have to be addressed and since about, there are annual reviews of waterborne disease outbreaks and their causes that are published.  Since about the late 1990s, the proportion of waterborne, these outbreaks that arise from distribution systems has been greater than the proportion that have arised [sic] from sources.  As treatment plants they’ve got better and more reliable.  It's been the networks that have been the bigger concern and the transgression reports that I've seen from health departments describing the transgressions, and some of these are published, I mean you can see those, some of those reports are showing again more E. coli’s, often the majority of the E. coli’s are thought to be due to ingress through water tanks or backflow events.

- Well that is why that recommendation, one of the reasons why that was put in?

- Yes so I think it is possibly not the most urgent of the bulk flow of water that needs to be treated but now that the treatment is in place and being improved, the residual risk in the distribution system, that then becomes a priority after time.

MR WILSON:

- And in the Hastings and the Havelock supply, given that you have got so many private bores on private property and you have got quite extensive private irrigation systems in both orchards and farms and New Zealanders propensity to do their own plumbing, there is a substantial risk of interconnection between the private and public network on private property and if you look at the historic literature, irrigation systems are often one of the causes of backflow as well.

- Absolutely, I think you are 100% correct and it is an area that there are standards and guidelines that give you advice on what the risk may be from the connection and what standard therefore of backflow prevention is higher standards, for higher risk and there should be a backflow prevention of some sort on every connection and where you have got a pressurised irrigation line for example, the standard is higher and so that is something – there is a function of Council that deals with that and has some catching up to do in that area.

- And my observation would be that in due course it would be timely for the District Council to review its entire policy on what level of backflow prevention is appropriate for each individual property for those reasons. I think the current policy is probably due for review.

- Yes my understanding is that is what I have been asked to include as part of the expansion of the Water Safety Plan to get those controls explicitly stated and make sure they meet good practice, current good practice.

JUSTICE STEVENS:

- I think that is really helpful.  So this is an area where an adjustment to the regs.

- Yes, Sir.

- Thank you Dr Deere, that is helpful.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Can we turn to the catchment.  Primarily around Brookvale Road, it has been about 10 months since the outbreak, would you expect the catchment area around Brookvale 3 to by now have been fully investigated and analysed?

- My understanding is it has been largely investigated by the hydrogeology.  So when I went to visit Tonkin & Taylor they explained they had been doing trace-off studies to try and understand the risk but there are some private properties.  So there are some areas that haven’t been forensically walked as it were and it is always a challenge in catchment so what Council has done is put in, for bores they are most concerned about, they have put in multiple barrier treatment, so filtration UV disinfection and chlorine disinfection, rather than just chlorine.  But the private property issues is if you don’t control those in a catchment zone, it is a big challenge.

- Would you accept that it is desirable to be aware of the presence of livestock in paddocks, neighbouring a water bore?

- It is both, the livestock issue and also that has no chemical removal process.  Also what kind of chemicals are applied such as herbicides and so on, pesticides.

MR WILSON:

- And by chemical removal processes, what processes are you talking about?

- Very few water supplies in this part of the world have them but in much of Northern Europe for example, it is routine to have ozone and carbon as a process to breakdown chemicals and then remove what is left that hasn’t broken down with carbon.  That is very unusual in Australasia to have those.  We tend to just manage chemicals by keeping them out of the catchment and so if you haven’t got a treatment process that can handle chemicals and you have got livestock, and you have got the mushroom farm; these sorts of things nearby, we need to be very confident they are not using hazardous chemicals on those sites.

JUSTICE STEVENS:

- And it also puts a premium on getting an accurate definition of catchment doesn’t it?

- Absolutely.

- You have got to know what your catchment is?

- Yes.

- And I think that was really where Mr Gedye’s question started out.  When you went to see Tonkin & Taylor, did their work – because we haven’t seen this yet.

- I see.

- Did it deal with the definition of catchment?

- At that point their focus was to understand what had caused the incident and focussed on that.  They are now looking at developing a model of the catchment and of solute and polluted transport, through the catchment so that they can work out what the zone of influence is, so that is work that is currently happening but I don’t think it is finished at this stage, that is my understanding.

CROSS-EXAMINATION CONTINUES:  mr gedye

- In your experience in your work in Australia and elsewhere, is it common to define or delineate a catchment area?

- It is for, yeah, it is usually considered essential to undertake two actions, one is to define a catchment area and then to conduct a sanitary inspection of that catchment and at periods re-do that inspection and the National Guidelines of New Zealand recommend that is done, that would be standard practice, has been for many years.

- Is it a concomitant of a catchment area that you have a catchment plan relating to that area?

- Correct, yeah, so there will be – usually it is just caused a Catchment Management Plan, but it's exactly what you are talk about, so it would have – it would lay out on usually these days on Geographical Information System, a GIS system, would lay out the defined catchment area, it would lay out the known pollution sources and I have seen some of the Regional Council they showed me the broader catchment of the aquifer as a whole, they showed me many of the bores that were present in the catchment but – and many of the land use activities, but they pointed out there are an unknown number of private bores on private land that haven't necessarily been plotted on there and other private activities that may not be known, because it is quite an active catchment or quite an active overlying area above the supposed aquitard.

JUSTICE STEVENS:

- Now of course, if you are going to have a strategy and a crucial element of that strategy is going to be do we persist with Brookvale 3.

- Yes.

- Defining the catchment for that Brookvale area is really a critical first step, isn't it?

- It is and often even if you haven't got a precise hydrogeological definition, you would use a rule of thumb to say, well, we’ll conservatively assume this is the catchment to start with, a larger area and then hopefully we can narrow that down, but in the absence of that narrowed down version we’ll assume it's the larger area and look at the pollution sources in that larger area.

- What – how do you define “larger area”?  Is it a 500 metres either way or what?  Give us a number.

- If I – I wouldn't be able to give a number, but if I were doing this, if I were asked the question, I’d go to the Regional Council who have the hydrogeological model of the system and ask them tell us what they know and see if we can get a sense of what's plausible, because they may be able to rule out some areas and say, “There is no way this area can be contributing, whereas these other areas could be contributing.”  If you pick a number, there are numbers that are used for microbiology so the Dutch are probably the world leaders in this.  They’ve established a 60 day travel time as a zone of influence for microorganisms, but – so that would be a 60 day hydraulic travel time from the surface to reach the bore and their view is microorganisms either just don’t live that long or get stuck and don’t get that far, so that’s been a value they have used.  There is – there are numbers you can use, but that requires a pretty good model to work at that bore scale and it is very difficult to do that.  So in the absence of that number, it would be more a professional judgment by the hydrogeological modeller and for many chemicals they can last much longer than 60 days so it can – as I said, the other day we had a problem in Katherine in Northern Territory, they had – they found toxic chemicals breaching the Guideline values that had travelled nine kilometres through the aquifer and breached Guideline values nine kilometres away, so for chemicals it is much more difficult.

MR WILSON:

- Dr Deere do you differentiate in any way between the terminology a source protection zone and a catchment?

- Yes, I do in that it is commonplace to have a nearby zone that is formally recognised as an inner catchment or a catchment protection zone or a special area.

- Or a source protection zone?

- Correct.  And there is – that then has special planning legislation associated with it, as distinct from the broader catchment that could be a river system 500 kilometres away.  You just can't do anything with that and you rely on dilution and time to try and mitigate the risk, but the closer you get the higher the risk and so it's very common to have an inner catchment area that has special plan – it has special planning overlays and special controls and it's usually of the order of a few kilometres of that order is quite significant, usually.

- And so it's obviously a sub-set of the catchment?

- Correct.

- And it has applicability in both surface water and groundwater sources?

- It does, yes.

- That was a question?

- Yes.

JUSTICE STEVENS:

- I think this has been a really helpful discussion and is directly relevant to the matters we were raising about strategy and prioritisation.

- Yes.

- And you may well need with Mr Thew’s concurrence, to understand just how much work Tonkin & Taylor have done and be ensuring that that is progressing fast.

- Yeah, yeah.  They have from Mr Thew is that Tonkin & Taylor are now looking at a modelling pathogens within the aquifer and how it influences the bores but I'm not, yeah, Mr Thew would be the one to ask about how that’s progressing.

- I understand.

CROSS-EXAMINATION CONTINUES:  mr gedye

- Coming back to bore 3, are you satisfied with the nature and extent of microbiological data being obtained from the BV3 water?

- I think now there's sufficient data being obtained, I think the key, as I said earlier, is to try now to prioritise the monitoring to events and therefore characterise what may change because I think we have enough data now to establish the baseline situation.  I think what's being monitored in the frequency has been more than sufficient to give us the evidence we need to get a sense of how vulnerable that bore is under normal circumstances but we have to wait until the events occur to find out what happens during events.

- How readily can you draw up a recommended monitoring programme from now on and can I preface that with reference to the Inquiry’s previous recommendations which were very simply expressed, which was two litre raw samples taken daily from each bore, total coliform and E. coli testing, enumerated tests for all reticulation samples, reticulation testing and so on.  What we want to achieve, hopefully by tomorrow, is a replacement set of two, three, four line instructions as to what to do and I think your view of what they should be will be critical and may simply be determinative because if you recommend it and HDC accepts it, the Panel may well think it can just be incorporated in the recommendation.  Can you draw that up tomorrow or by tomorrow?

- Yes, I've already edited a draft revised monitoring programme that Council’s been working on and so I think we would just find a way of summarising that because my understanding is that there's an agreement to continue I think the use of the higher volume test that Dr Fricker recommended as a good idea because it's more sensitive and gives you an early warning.  So I think that, as I say, is a good idea.  What we've changed is recommendation to move to a more fit for purpose frequency that will pick up events but I think we can write that in a short, there's a short form version, a table version of that.  The only complication is some bores we've recommended slightly more testing than others for reasons related to risk and knowledge, which might make a slight complication in a very short summary but it wouldn’t be difficult to summarise that.

- If it's already in table form, the Inquiry could readily recommend that monitoring take place in accordance with the table annexed –

- Okay.

- – or table X, Y, Z.

- Yeah.

JUSTICE STEVENS:

- And what this would do, Dr Deere, is essentially replace recommendation J.

- Okay.

- Page 158 of the –

CROSS-EXAMINATION CONTINUES:  mr gedye

- J, K and L.

- Okay, good and that would be straightforward to do that and it's easier for us to provide a table than try and write in paragraph form.

- Subject to what the Panel says, I would have thought a table is a very clear and compendious way to do it.

- Yep.

- But can I just explore a little?  There's been two main components.  One is the two litre E. coli testing and the other is the Protozoa testing.

- Yes.

- Sticking first with the two litre E. coli testing, would it be your recommendation that that now does not need to be taken daily from each bore and that it could be deployed only when there's a wet weather event?

- I think there would be still be some baseline from each bore but it would, a frequency of weekly for instance would be more than sufficient at this point and then it would be deployed at a higher frequency during wet weather events.

- Something like three times a day or?

- That would be a quite – to get an achievable frequency, we’d have to check what the lab can handle in terms of their capacity but I think that would be achievable.

- Well, this is what we've come down to now.  We have currently two litre samples daily from each bore.  What do you think it should be in future and you might want to reflect on that overnight.  Should it be weekly, fortnightly?

- I would be uncomfortable less than a weekly, even though the guidelines talk about 45-day intervals, for a drinking water bore, that to me less than weekly is a frequency that is below what I consider benchmark and maybe over time we would drop it but for the next step, I wouldn't drop below weekly.

- And would you do total coliform of E. coli testing presence/absence testing only for those?

- If we hadn't had a history of counts, and there's a significant difference in cost, we could justify presence/absence testing.  Often the cost difference is small enough that we may as well get the enumeration but if it's a significant difference in cost, I'd accept presence/absence testing as being adequate.

- Can I just press pause and say that these recommendations were outside and in addition to the standard DWSNZ regulated testing regime, query whether you want to be looking at a monitoring regime which merges the two, my point being, these two litre samples were in addition to the 100 mil samples that are taken in accordance with the DWSNZ.

- Correct.

- Are you in fact looking at a regime which merges the investigative sampling and the regulated sampling?

- I think we would still want to have some investigative sampling, albeit on lower frequency to get better characterisation 'cos we haven't been through enough events yet to be confident.  The benchmark time periods we're talking about are usually a couple of years.  Until we've reached a confidence where we drop down a long-term norm, so for perhaps another year and a half, we’d maintain an elevated frequency above the standard requirements.

- But the DWSNZ 100 mil samples and I think they're being enumerated –

- Correct.

- – by choice by HDC.  So you'd keep doing the 100 mil enumerated’s?

- As compliant samples, yes.

- Yes, but you'd add in two litre presence/absence samples weekly?

- As operational samples, yes and that’s whether the drinking water regulator considers those to be compliant samples is their decision but from Council’s point of view, they are just trying to better characterise the bores and characterise what conditions lead to elevated counts in those bores.

- The only caution about this about your table is the table may not make this adequately clear.  I don’t know.

- The draft table that we had was designed to be one you could pull out and give to the lab and say this is the programme.  So it would be clear although I don’t think that, the point about compliance was clear.  So yeah, that’s a good question about whether it's a compliance requirement as per the standards.  It's a good question.  I don’t know if that’s clear in the table.

MR WILSON:

- Dr Deere, my understanding is for compliance all that is required is a test that complies with the appropriate sampling and testing regime.  Whether it is 100 millimetres or two litres, I think does not matter in the slightest.  It is whether or not it has got E. coli.

- That’s correct, although what we were trying to do was give Council the option to conduct operational testing without the complication that comes with compliance testing to encourage operational testing and then separately say these are our routine compliance samples that we report in our routine compliance, otherwise the danger would be Councils don’t do testing because they're afraid it'll get added to the, the more testing you do the more you find.  So trying to encourage the freedom to do lots of extra investigative testing without potentially making yourself look bad in your compliance report.  So it's common practice to have a compliance programme that’s seen as separate from your operational programme, even though scientifically it's the same thing.  It's just the monitoring.

- But the other point with the compliance programme is that it must occur on different days of the week and it must occur –

- Correct.

- – in different parts of the network but also notwithstanding what you are saying, if you pick up a positive as part of a what you call operational testing, you still have an obligation to report it to –

- Correct.

- – the regulator?

- You still respond and report to it but in your report on your performance, you'd use the compliance samples for your annual performance report and you'd leave your raw water operational samples as your, just what they are, they're operational samples.  You'd report the results but they're not given, they're not in your end of year mark book as your end of year score.

- Pure logic.

- Yeah, it's purely to, we don’t want to put a disincentive to Councils to do extra monitoring and if we, because you will get a proportion of positives, we’d like to try to keep the operational separate from the compliance and it's a common practice to avoid that perverse sort of perverse incentive.

JUSTICE STEVENS:

- And we follow that and I think it is wise.  So you are working with Mr Thew on this?

- Mainly Mr Chapman with Mr Thew overseeing it, yes.

- Well, that’s great.  If you could provide a replacement for J, K and L to Mr Gedye –

- Yes.

- – in the morning, then he’ll discuss with Ms Casey.

- Yes.  And as I said, there will be the two – there’s a sort of a next phase, it drops down again and then there’ll be a proposed, if all goes well, the proposed long-term sort of indefinite phase after that.

- No, very sound.

CROSS-EXAMINATION CONTINUES:  Mr Gedye

- Just quickly on the Protozoa testing, do you support that continuing on a weekly basis through to spring or would stop that now and only activate that on wet weather events?

- I think where’s there is treatment in place that can manage Protozoa, I think there is little value in continuing of that.  Where there is no treatment in place for Protozoa and we are relying on the bore security, I think it will have to continue.  The baseline programme can drop in frequency but we – the events are the focus and once again it would be – the precedents that I have seen in other Regulations and Guidelines by expert committees, they talk about at least two years of data before you make a decision on what your level of risk is.  So think again part of that sort of next year and a half will have that continue, albeit costly, to characterise – if there’s a decision to put in Protozoa treatment barriers, that would obviate the need for that testing on the grounds that you’re treating them anyway.

- So on BV3, you wouldn't need ongoing Protozoa testing, but on all of the other Hastings bores you would?

- At this point in time, yes.  At this point in time we don’t have enough history, particularly for events, to know if those are vulnerable for Protozoa and get a sense of if they are vulnerable to Protozoa.  Therefore we haven't got a basis to say no need to treat for them, but so the dividend for doing that extra monitoring could be justifying not treating for them, but if there is no treatment – if the decision is made to treat for them then that avoids the need for the testing.

- And it sounds like installing UV could end up being a cost-effective option compared with the cost of Protozoa testing for a year and a half?

- If that’s the case and often for small suppliers the package customise – the packaged off-the-shelf UV systems are often relatively affordable, they’re extremely effective on Protozoa and as a result if they – that costs the same as testing, there’ll be no logic to test, you may as well just treat them, yeah.

MR WILSON:

- And by “cost-effective” you mean both in terms of capital and operating costs?

- Correct.  I mean, the Protozoa testing is surprisingly expensive, unfortunately, and it has limited value in that even the best testing, they’re only going to sample once per week or once per month, it's not going to be continuous whereas obviously the UV system is continuously there killing any Protozoa that get through.

- Dr Deere, something that you may be able to elucidate, tell me are their different levels of energy required by UV systems to treat Protozoa versus bacteria?

- The Protozoa and bacteria have similar responses to UV disinfection and so usually the Protozoa is used as the organism of the target organism and then we get more than enough kill for the bacteria so that’s – yes, sorry –

- And what about viruses?

- Viruses have a – it depends on the type of light you use.  If you use what's called “low pressure UV disinfectant” which most is low-pressure lamps, I don’t understand the engineering behind that, but they talk about “low-pressure lamps,” the wavelength of light is limited to one wavelength and it's not very good on viruses, you need much, much higher doses to inactivate viruses, whereas with the medium-pressure lamp UV systems, the German ones often use a medium-pressure which has – I don’t know why they’re called “medium-pressure,” I don’t know what the engineering is behind that – but they’re called “medium-pressure lamps,” they have a lot more different types of light and they’re very good on viruses, as well as Protozoa.  So it depends on the unit.  Where you’ve got – if we’ve got risks where there’s humans in the area as we have in the bores in the middle of the city, there are people, there are sewer pipes and so-on, and you are concerned of possibility of virus risk, you might be better to go down the path of a medum-pressure UV system and many Councils have gone for those.  Then you have a cost-effective reliable treatment.

- Or alternatively, you go for a low-pressure system and chlorine?

- Correct.  Chlorine is highly effective on viruses, so yes, if you have as you say low-pressure low-cost UV system with chlorine then with the kind of groundwater that with the kind of turbidity levels that this Council’s receiving, it's not likely you would ever see a significant health risk getting through those systems.

- By the way, I think it relates to the pressure inside the bulb.

- I am assuming so, yeah, but I don’t know why they’re called “low and medium-pressure,” I don’t know what “high-pressure” is either, but that's what – that’s the term that is used in the industry, so.

JUSTICE STEVENS:

- All of this discussion is relevant to strategy.

- Yes.

- Of course and it's also arising in the context that you described to us earlier today about the unusual circumstance of these bores being very close to sewage assets.

- Yes, generally speaking, because the Water Utility owns the sewage and the water assets, they tend to stick their bores well away from sewage assets and then have a protection zone that you can't – where you can't have septic tanks or you only have special pump-out systems or pressure sewers, other things.  So for that reason – no, not the case here.

- No.

- So on – in the Australia Committee where – when this was discussed, the view was that it's highly unlikely you would have anybody with a drinking water bore close to sewage assets and if that had, ideally they’d move it was the preferred option for that reason, so this is –

MR WILSON:

- Move the bore?

- Remove – yeah, move the bore and pump from somewhere else, away from a sewage asset.  And because most people control both, they know where the sewage assets are and they can control that.

JUSTICE STEVENS:

Okay, that’s been very helpful.  Mr Gedye?

MR GEDYE:

Yes, that completes the questions I have, thank you, Your Honour.

QUESTIONS FROM THE PANEL:  Dr Poutasi

- Just to clarify, I don’t think we quite landed it, but I think you were saying that the Protozoal testing could drop in frequency and be intensified around adverse weather and events, would you – you would recommend that?

- Correct, there’s enough – there appears to be enough data now that we’re not seeing routine Protozoa detections during the normal conditions, and so it's futile testing more.  What we want to catch is the highest risk is spring, spring where you have lambing season, calving season, and heavy rain.  That’s the period you want to get through, this spring, before we’re comfortable to back off on that.

QUESTIONS FROM THE PANEL:  MR WILSON

- But where there is no barrier in the city bores where they are close to sewers, you think there should still be a regular baseline testing?

- If the decision is made to rely on the sewage, the sewage assets and the aquitard and the groundwater movement of the barrier, because there is definitely a risk with , those sewers are full of Protozoa.  If that is a decision that’s made not to put treatment on and there’d have to be ongoing evidence that they’re not breaking through.  There’s no way you could stop that because that’s your only evidence you’ve got to show they’re not breaking through.  But if the decision is made to treat for Protozoa then it would be unnecessary to test as well.

- It's –

QUESTIONS FROM THE panel:  JUSTICE STEVENS

- All right, so they’re linked?

- Yes.  So it's a strategic question, I suppose.

- So there’s some strategy.

- Yeah.

- That’s why I brought it up again because that’s where we started.

- Yes.

- And that's where end and obviously you will be talking to Mr Thew about that.

JUSTICE STEVENS:

I have no further questions, but I do want to address you after I have checked with counsel.

QUESTIONS ARISING: Ms ridder – NIL

QUESTIONS ARISING: Mr Matheson – NIL

QUESTIONS ARISING: Ms arapere – NIL

QUESTIONS ARISING:  Ms Casey

- Just some general questions, thank you, Dr Deere.  Am I – oh, no, actually I’m all right – would it be correct to say that you’re working with the District Council on helping them, showing them how to get their system to global best practice?

- Correct and it's actually been interesting.  Some of the – because Mr Thew has a background outside of water industry, he’s showing me some examples of good practices that the water industry hasn’t adopted that they could, so hopefully it will go slightly beyond that, but we will see how we go.

- Leading global best practice, perhaps.

- Yes, yes, but that’s correct, that’s what they’ve asked to be at the benchmark standard.

- And they’ve brought you in to assist with that guiding process because that guide is not currently available on the Drinking Water Standards?

- The – some of those practices are not – they’re not in the templates that are available on the Health Department’s – Ministry of Health’s website, they’re missing from there, but they are available in other forms, but it's about having the practical experience to interpret those for Council, that’s why I'm coming in for really.

- Does – just to clarify there, when I’m talking about the Drinking Water Standards I am talking about it's not a – the material that you’re introducing now is not a requirement under the current Regulations?

- It's not a requirement nor is their guidance on how to provide it, so both are missing.  You can get the guidance from international guidance, but turning that into something practical is – I can help that just from facilitation sort of side of helping them do that quickly and providing a resource to help do that in a short timeframe.

- Oh, absolutely and obviously of huge value.  So and just stepping back, was your view that they were operating a system that was compliant with the Regulations at the time of the August outbreak?

- The material that I saw, the water safety plan that I saw that was from that time was actually slightly above the level that would be required to be adequate under the Regulations.  So I wasn’t surprised that the assessor found it to be adequate.  What I did say is it wouldn’t be adequate in many other jurisdictions because it missed some key points but it was adequate under the local jurisdiction.

- And just because we've been talking a lot of about improvements and that long-term improvements and work plans and we've been talking about the work that the Council’s undertaking to better understand its water sources, in your opinion, is there any current issue with the safety of the drinking water at the moment?

- By the time I was engaged in around February and visiting in April, there was nothing that concerned me in terms of immediate water safety no.  There's a need to improve some of the temporary systems and make them better quality permanent systems that’s being worked on.  There's tenders and things being carried out.  There's a need to improve the reliability.  I think that Mr Wilson’s point about the long-term reliability and avoiding complacency and that’s going on but the actual immediate risk is managed.

- Thank you.

- The test that I apply in my mind when I go do audits or risk assessments for Councils is would I let my little daughter or my 80 year old father drink this water and, you know, in my mind the answer was yes I would and so that was in my mind I felt comfortable saying, you know, the water is safe right now that the Council is supplying but I'd like to see improvements in terms of the system management to look at it and make it more reliable for the long-term and that’s what Council’s working on.

JUSTICE STEVENS:

- Thank you.  Now, Dr Deere, I did mention yesterday when I spoke to you that we appreciated that you had other competing commitments this week and changed those in order to be here and on behalf of the Panel, I wanted to acknowledge the fact that you did that and to say that we have really appreciated your presence and your expertise and the way in which you have given your evidence.  So thank you.

- And I'll just say that it was no trouble for me.  Just it was the Cairns Regional Council, it was them who moved their so for me it's no problem at all.

- Well, that is good.

- So I have got to acknowledge Cairns Regional Council’s water quality co-ordinator for moving her training session back a few weeks.  It wasn’t a big problem for her but she was happy to do it and so I just want to acknowledge her doing that and re-organising those people.

- You can pass on our thanks to the Cairns Council.

- Thank you, I will do.

- Now, I am not sure, obviously there is some work-ons overnight and you will be visiting the labs and will we expect to see you again in the August hearing, the 7th of August?  Are you scheduled to return?

- I haven't been asked to but Mr Thew has asked me if I'm available that week.  I'm available that week so I'll await my instructions.  If I'm asked to attend, I'll attend with Mr Thew and his colleagues.

- All I would say on behalf of the Panel is that there are matters that have arisen in the context of this Inquiry, which is focusing on issues 1 and 2, on the immediate safety of the drinking water, which you have been very responsible on, but you have rightly raised other matters that I think we could usefully develop in August.  So if and to the extent that you are available, we will look forward to seeing you again then.

- Okay.  No problem.

- And any of the documentation, those papers that you mentioned, if you could make arrangements to send them to both Ms Casey and counsel assisting.

- I will.  Yeah, there are some that I consider seminal classic papers in the industry that will be good for you to see those papers.

JUSTICE STEVENS TO MR GEDYE:

- Now, Mr Gedye is going to be away for a period, so do you want to arrange with all other counsel tomorrow to ensure that the chain of communication is not lost while you are away?

- Yes, I will.  I think if the Inquiry email address is used, as well as mine, that will ensure they are reached in a timely way.

- With perhaps Ms Cuncannon could be included in the distribution.

- Yes, I'll send out a note indicating that.

- Yes.  And there was one other matter that we were going to raise I think with Ms Arapere relevant to Dr Deere’s work.  Can you remember what that was, Mr Gedye?

- No, I can't.

- No.  I mean the main point was capturing the international best practice that you have alerted us to and maybe it will flow out the papers that you forward to –

- The early piece was all about water safety plan guides.

- Yes.

- And they're all on the Inquiry website as common bundle number CB216 to about 227.  It's a series of guidebooks and guide documents.

- Yes.

- And Dr Deere referred to the WHO, he talked about a portal which – is that on the website.

- Okay.  I now remember.

DR DEERE:

WSP portal, yes, that’s correct.

JUSTICE STEVENS TO MS ARAPERE:

- I have now remembered what it was and it was in that area.  Ms Arapere, it would be helpful to know soon, I mean obviously the Ministry has access to all of that material.  It will be aware of where the current World Health Organisation Drinking Water Standards requirements sit and we have heard today from Dr Deere that they represent industry best practice and the implication is that obviously if asked, he as an expert witness would support recommendations from the Panel that the New Zealand Drinking Water Standards be improved to meet current World Health Organisation Guidelines.

- Yes, Sir.  This morning I took a note when we had that earlier exchange to seek instructions from the Ministry on that to be addressed in the 21 July paper.

- Yes, but what I really would like to know is presumably there would not be any pushback from the Ministry on that and it would help if we did not have to, and that is nearly a month away, if we did not have to wait until the 21st of July to find out that the Ministry endorses the concept of moving to World Health Organisation Standards.

- Ms Butler had a conversation with the Ministry this morning and they are, they want to assist the Inquiry in any way they can.  They are open to recommendations that they improve whatever water safety plan guidelines they currently have.  There is no pushback as we understand it, Sir, but we wanted to be in a position to file something in writing.

- Of course.  No, that is great.

- Yes.

- And again, just let me put it this way and it is to all parties here.  In stage 2, we have a unique opportunity to contribute to a world-class system of management of drinking water in this country and although it is being done in the context of the events of August last year, and in the context of the stage 1 report, it is obviously already having significant implications and benefits across the country and we want to make sure that we get the very best result we can.  So hopefully, it is a proactive endorsement and if one can move further ahead or if there is something better, then let us hear it from the Ministry.

MR WILSON:

If I may – might make a comment on that.

MS ARAPERE:

Yes Sir.

MR WILSON:

You know, the current legislation obliges the, or requires, the Ministry to consult for a minimum of three years on any amendments to the drinking water – I think it's three, it's at least three –

MS ARAPERE:

I think it is three, yes.

MR WILSON:

And then once gazetted, for – it's at least 12 months before – or was it two years before they take affect.

MR GEDYE:

Two years.

MR WILSON:

Which is not very helpful, given that we now know they are at least 10 years out of date.

MS ARAPERE:

Ten years behind, mhm.

MR WILSON:

And in particular, it is not helpful in that we now know that science tells us that there is cheaper solutions to address Protozoa than are currently recognised in the Drinking Water Standards.  Obviously, if the Ministry has a view on how unhelpful that is, it would be useful.

MS ARAPERE:

Yes, no, that’s heard and understood and we are seeking instructions on those things.  We will come back to you sooner than the 21st of July if we possibly can.

JUSTICE STEVENS:

That would be really helpful.

QUESTIONS ARISING: Mr Gedye – NIL

JUSTICE STEVENS:

- Very well, it remains to release you, thank you for your attendance and hopefully we will see you in August again.

- Thank you, just one final comment if I may just quickly, is that you will be interested there is a lot New Zealand experts named in those WHO Guidelines, a significant number, so you’ve – there’s expertise locally to – or is available for that sort of work.

- That does remind me, thank you.

- Okay.

MR WILSON:

Now I have remembered it, too.

FURTHER QUESTIONS FROM THE PANEL:  JUSTICE STEVENS

- Now I remember another point that we had been reflecting about was the name Dr Noakes one of those?

- Yes.

- Yes.

- Yes, Absolutely.

JUSTICE STEVENS:

All right, now where is Dr Noakes, Ms Arapere?  Why haven't we heard from him and what are you doing to make sure that as someone who has contributed significantly to the scientific and international endeavour here, he is not helping us?

MS ARAPERE:

If Mr Noakes or Dr Noakes is the person I am thinking of Sir, he is no longer a Ministry employee.

JUSTICE STEVENS:

Well, no, I think he works for the ESR.

MS ARAPERE:

ESR yes.

MR WILSON:

I don’t think he was ever an employee of the Ministry.

MS ARAPERE:

Oh, I must be thinking of another expert who was within the Ministry who is no longer.

JUSTICE STEVENS:

This is – is it Dr Chris Noakes is the –

DR DEERE:

Yeah, he was with ESR, yeah, I actually don’t know if he’s still there, but he was with ESR.

MR WILSON:

I think you are thinking of Mr Graham, probably, who is no longer with the Ministry.

DR DEERE:

He is also named in a lot of those documents, WHO documents as well.

MS ARAPERE:

Apologies, that is who I was thinking of.

DR DEERE:

Yeah, he’s also a big name in the documents, yeah.

JUSTICE STEVENS:

All right, so –

MS ARAPERE:

We will take that back on my very long list of things to do Sir, to the Ministry.

JUSTICE STEVENS:

Take that under advisement.  I mean, if it is – it would help you, we could – I could speak to Head of Secretariat and ask for a subpoena to be issued.

MS ARAPERE:

Let me see what I can do overnight on that, yes.

JUSTICE STEVENS:

But hopefully that won't be necessary and I mean that some of the reports that we have read are – by Dr Noakes are outstanding and he is an obvious expert.  We’ve had the benefit of input from Dr Fricker.  We have now heard from Dr Deere who is a world class expert and why haven't we got our own home-grown expert contributing?

MS ARAPERE:

I will see what I can do overnight Sir.

JUSTICE STEVENS:

That would be great.  Now, does that cover it, Mr Gedye?

FURTHER QUESTIONS ARISING:  MR GEDYE:

- Yes, it does, but I just wanted to ask Dr Deere, is there anyone else within ESR or maybe NIWA or in New Zealand that springs to your mind as someone who has particular expertise that we should be hearing from?

- The people that advised us in Australia when were developing our system and that advised WHO and that also did a lot of work for the Aid Agencies in the Pacific Islands for WHO in training Water Safety Plan were people like Dr Chris Noakes, Jim Graham, Jan Gregor, Marianne Saville has been involved, they’re probably the main names that come to mind as people we’ve regularly been in touch with.  Obviously Michael Taylor but he is now retired.  And Graham McBride was involved a lot in the statistical side, but I believe he has also retired, I’m not sure if that  is correct, but they others would still be working, I think.

- I think we have the benefit through Water New Zealand of Jim Graham and –

MR WILSON:

Graham McBride.

FURTHER QUESTIONS ARISING CONTINUES:  Mr Gedye

- – Mr McBride, yes.

- Yep.  So they’re the people that were heavily involved and have been – continue to be involved with the aid work that New Zealand and Australia has funded in the region through the Western Pacific Regional Office doing training and water safety plans against WHO, so they’re very familiar with WHO guidelines and have been training in that area in the islands.

JUSTICE STEVENS TO MS ARAPERE:

- All right.  That gives you a heads-up there, Ms Arapere.

- Thank you, Sir, yes.  We have a long list now.  Sorry, the name I was searching for was David Ogilvy who was in the Ministry.

- Okay.  Yes, that is another –

MR WILSON:

Yes, David is retired.  He is in 80s but still active.

JUSTICE STEVENS:

Very good.  Well, we do not need to worry about ageism but –

DR DEERE:

And Wellington based.

JUSTICE STEVENS TO MR GEDYE:

- Yes.  So, Mr Gedye, that brings us to the end of the day.

- Shall we speak briefly about tomorrow, Sir.

- Yes, I would like to do that.  Dr Jones is keen to get on.

- Dr Jones and Mr Maxwell.

- Yes.

- I think we could start at 10 without too much fear of running out of time unless you –

- Well, that would allow Dr Deere to continue his discussions on the framing of the consent recommendations or undertakings.  I just do not want to put us under pressure.  So maybe 9.30.  Would 9.30 work?  Would you start with Dr Jones?

- Yes, either him or Mr Maxwell but Dr Jones, yes.  Mr Maxwell has gone but he said he was reasonably flexible.

- Mr Maxwell, he will be available then?

MR MATHESON:

Yes, I can answer that, Sir, thank you.  Yes, he had to leave briefly this afternoon.  He's free all day tomorrow so we can have him here whenever suits, Sir.

MR GEDYE:

Yeah, 9.30 would safely get those two witnesses done plus time for…

JUSTICE STEVENS:

What I anticipate is that we will finish the evidence and questions by 11 and then maybe an hour, have a morning adjournment break and then leave counsel to work together on variations to the recommendations and undertakings from relevant parties to ensure that the work streams that have been discussed flowing out of the joint working group and those recommendations can continue in such a way as they will be useful to the Inquiry and be able to be incorporated to the extent necessary into our recommendations.

MR GEDYE:

Yes, that all sounds good, Sir.

JUSTICE STEVENS:

Very well.  Well, thank you all and we will look forward to seeing you in the morning at 9.30.  Thank you, Mr Registrar.

INQUIRY ADJOURNS:	5.27 pm